## oq25vcrBH
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34676 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 14960 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34676 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7258 | 1.6117 | N1 | 12.4123 | 3.9777 | N | 14.6633 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 14960 | 0 | 1 | N-0 | 8.62 | 114.37 | N2 | 10.1021 | 3.1056 | N1 | 8.684 | 1.1914 | N | 8.6212 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25baseBH
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34676 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34150 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34676 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7258 | 1.6117 | N1 | 12.4123 | 3.9777 | N | 14.6633 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34150 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.1503 | 2.4 | N1 | 8.7069 | 1.1914 | N | 10.816 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25base_bsp96LDC
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.55 | 34747 | 1 | 1 | 1 | 1 | 0.979 | 0.781 | 0.291 | 0.085 | 0.018 | 0.018 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-1 | 1.74 | 1.49 | N2 | 2.0628 | 0.35737 | N1 | 1.7389 | 1.486 | N | 2.0311 | 18.7344 | 0 | 0 | 0 | 0 | 0.2 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25basecase
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
Wellington Town | 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.447 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25basecaser1
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150 | [15 empty] | max mins
| 3 | 1.5 | 1.5 | 1 | 1 | 300 | [15 empty] | 16.422
BSP | data | [20 empty] | non-catastrophic transformer failure
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ... | [8 empty] | mins EUE | MWh EUE | LDC lookup | res1 | curr std N-?
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0 |  | 1.2936 | 0.31706 | 0.764 | 1 | 1
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0 |  | 10.2 | 0.2754 | 1 | 3 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0 |  | 1.5391 | 5.1017 | 0.606 | 1 | 2
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0 |  | 1.2479 | 0.7687 | 0.737 | 1 | 1
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0 |  | 14.586 | 1.0891 | 0.715 | 3 | -1
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0 |  | 14.586 | 2.042 | 0.715 | 3 | -1
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0 |  | 1.6932 | 0.27373 | 1 | 1 | -1
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0 |  | 0.75855 | 0.2306 | 0.448 | 1 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0 |  | 0 | 0 | #DIV/0! | 1 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0 |  | 0.72469 | 2.8897 | 0.214 | 1 | 1
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0 |  | 0 | 0 | #DIV/0! | 1 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0 |  | 5.9364 | 2.5485 | 0.388 | 2 | 1
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0 |  | 0 | 0 | #DIV/0! | 3 | 1
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0 |  | 5.9823 | 0.69993 | 0.391 | 2 | -1
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0 |  | 0 | 0 | 0.042 | 0 | 1
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0 |  | 5.6916 | 1.2319 | 0.279 | 3 | 1
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0 |  | 0.95496 | 5.9073 | 0.282 | 1 | 1
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0 |  | 1.6864 | 0.44522 | 0.996 | 1 | 1
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0 |  | 1.1344 | 0.45194 | 0.67 | 1 | 1
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0 |  | 0.85168 | 0.12311 | 0.503 | 1 | 1
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0 |  | 1.0955 | 0.30367 | 0.647 | 1 | 1
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0 |  | 1.5544 | 0.94816 | 0.918 | 1 | 1
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0 |  | 12.9948 | 0.93563 | 0.637 | 3 | 1
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0 |  | 0.34033 | 0.21328 | 0.134 | 1 | 1
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0 |  | 1.0278 | 0.22357 | 0.607 | 1 | 1
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0 |  | 0.68575 | 2.4467 | 0.27 | 1 | 2
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0 |  | 0 | 0 | #DIV/0! | 2 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0 |  | 0 | 0 | 0.406 | 0 | 1
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0 |  | 0 | 0 | #DIV/0! | 2 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0 |  | 0.79411 | 0.88269 | 0.469 | 1 | 1
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0 |  | 9.3024 | 2.6589 | 0.456 | 3 | 1
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0 |  | 16.422 | 3.6479 | 0.805 | 3 | 1
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0 |  | 2.6928 | 1.0659 | 0.176 | 2 | 1
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0 |  | 0.97867 | 0.90429 | 0.578 | 1 | 1
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0 |  | 1.0863 | 2.8348 | 0.071 | 2 | 1
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0 |  | 0.8466 | 1.0743 | 1 | 1 | 1
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0 |  | 0.8466 | 1.0743 | 1 | 1 | 1
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0 |  | 0.8466 | 0.896 | 1 | 1 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0 |  | 10.2 | 0.35547 | 1 | 3 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0 |  | 1.1175 | 0.26653 | 0.66 | 1 | 1
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0 |  | 1.0955 | 0.37521 | 0.647 | 1 | 1
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0 |  | 0 | 0 | #DIV/0! | 1 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0 |  | 0.8466 | 0.65487 | 1 | 1 | 1
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0 |  | 0.5232 | 0.46809 | 0.309 | 1 | -1
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0 |  | 5.508 | 0.031396 | 0.27 | 3 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0 |  | 1.109 | 0.34876 | 0.655 | 1 | 1
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0 |  | 0.77887 | 1.5048 | 0.46 | 1 | 1
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0 |  | 11.016 | 0.51279 | 0.54 | 3 | 1
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0 |  | 1.2106 | 0.49717 | 0.715 | 1 | 1
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0 |  | 0.17525 | 0.40935 | 0.069 | 1 | 1
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0 |  | 2.3315 | 4.1293 | 0.918 | 1 | 1
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0 |  | 0.93465 | 0.40881 | 0.368 | 1 | 1
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0 |  | 1.3038 | 0.71342 | 0.77 | 1 | 1
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0 |  | 7.9356 | 1.5453 | 0.389 | 3 | 1
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0 |  | 0.65019 | 0.31531 | 0.256 | 1 | 1
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0 |  | 1.0599 | 0.58057 | 0.626 | 1 | 1
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0 |  | 0 | 0 | #DIV/0! | 2 | 1
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0 |  | 0.19641 | 0.32012 | 0.116 | 1 | 1
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0 |  | 0.68575 | 1.5361 | 0.27 | 1 | 2
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0 |  | 0 | 0 | #DIV/0! | 0 | 1
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0 |  | 0.4978 | 2.2991 | 0.147 | 1 | 1
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0 |  | 0.21588 | 1.5623 | 0.051 | 1 | 2
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0 |  | 0.17271 | 1.5753 | 0.034 | 1 | 2
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0 |  | 0.093126 | 0.79065 | 0.022 | 1 | 1
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0 |  | 1.0193 | 0.89577 | 0.602 | 1 | 1
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0 |  | 8.16 | 1.5341 | 0.4 | 3 | 1
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0 |  | 1.1615 | 0.48223 | 0.686 | 1 | 1
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0 |  | 15.3612 | 0.71506 | 0.753 | 3 | 1
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0 |  | 2.5398 | 8.6103 | 1 | 1 | 1
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0 |  | 3.3627 | 52.4772 | 0.993 | 1 | 1
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0 |  | 0.64172 | 0.83886 | 0.379 | 1 | 1
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0 |  | 1.3969 | 0.4423 | 0.825 | 1 | 1
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0 |  | 0.61294 | 0.37382 | 0.362 | 1 | 1
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0 |  | 0.13715 | 0.34657 | 0.054 | 1 | 1
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0 |  | 5.6304 | 2.5853 | 0.184 | 3 | 1
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0 |  | 0 | 0 | #DIV/0! | 1 | 1
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0 |  | 10.2 | 1.3178 | 1 | 3 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0 |  | 0 | 0 | 0.11 | 0 | 1
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0 |  | 0 | 0 | 0.421 | 0 | 1
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0 |  | 0.63495 | 0.82156 | 0.375 | 1 | 1
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0 |  | 1.3732 | 2.1407 | 0.811 | 1 | 1
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0 |  | 0 | 0 | #DIV/0! | 3 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0 |  | 1.1954 | 1.9724 | 0.706 | 1 | 1
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0 |  | 13.77 | 4.5735 | 0.675 | 3 | 1
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0 |  | 0 | 0 | #DIV/0! | 2 | -1
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0 |  | 10.9548 | 1.1174 | 0.537 | 3 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N | r2 | r1
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 3
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 3
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 2
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 3
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 2
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0 | 0 | 3
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 3
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 1
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 1
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0 | 0 | 3
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0 | 0 | 1
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 3
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 2
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 1
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0 | 0 | 3
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 3
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 2
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 2
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0 | 0 | 1
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 1
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0 | 0 | 3
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 3
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0 | 0 | 1
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 1
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0 | 0 | 1
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 3
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 3
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0 | 0 | 3
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 2
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 1
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 3
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0 | 0 | 3
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 3
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 1
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 1
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0 | 0 | 3
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0 | 0 | 3
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0 | 0 | 3
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 3

## oq25aemovcr
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 38808 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 38808 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 38808 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 38808 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 38808 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 38808.21 | 3 | 1 | N-1 | 28.41 | 6.99 | N2 | 32.638 | 0.5367 | N1 | 28.4064 | 6.9859 | N | 36.3307 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 38808.21 | 3 | 1 | N-1 | 32.48 | 9.18 | N2 | 37.2983 | 1.3908 | N1 | 32.4775 | 9.1753 | N | 39.8536 | 335.5287 | 0 | 0 | 0 | 0 | 0.1 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.35 | 57.28 | N2 | 75.7009 | 1.0828 | N1 | 66.3547 | 57.2802 | N | 66.5463 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 38808.21 | 3 | 2 | N-1 | 27.41 | 10.02 | N2 | 27.6694 | 1.9485 | N1 | 27.4098 | 10.0207 | N | 33.0816 | 212.9358 | 0 | 0 | 0 | 0 | 0.1 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 38808.21 | 5 | 6 | N-1 | 14.83 | 3.09 | N2 | 14.8334 | 3.0843 | N1 | 14.8328 | 3.0856 | N | 16.2188 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 38808.21 | 6 | 6 | N-1 | 17.18 | 2.88 | N2 | 17.2091 | 2.8766 | N1 | 17.1778 | 2.8781 | N | 18.42 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25VCR70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 25283 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 4235 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 24379 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 23655 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 23817 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 23685 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 4235 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 4235 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 27655 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 24101 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 24101 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 26095 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 24677 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 25461 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 26716 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 24050 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 24050 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 24050 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 23682 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 27702 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 26384 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 24883 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 24159 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 24822 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 24822 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 24305 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 4235 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 24103 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 25678 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 25447 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 22994 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 26845 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 28455 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 26845 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 27405 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 23973 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 24285 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 24600 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 28148 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 25202 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 25431 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 26155 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 26155 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 24656 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 23773 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 25805 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 22524 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 26003 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 26845 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 26881 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 24018 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 24871 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 24871 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 27975 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 20520 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 24263 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 28148 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 23643 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 25259 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 27655 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 24057 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 24057 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 24481 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 4235 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 23950 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 24536 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 22929 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 23766 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 25442 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 31184 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 23072 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 25866 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 26974 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 25375 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 24434 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 24434 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 23724 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 27655 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 4235 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 24871 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 23798 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 24871 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 24883 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 24389 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 24389 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 24389 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 23859 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 23859 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 27655 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 24323 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 24323 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 26095 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 25140 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 22806 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 22806 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 25283.03 | 0 | 3 | N-1 | 10.22 | 20.69 | N2 | 10.4328 | 0.69847 | N1 | 10.22 | 20.6949 | N | 10.8041 | 49.968 | 0 | 0 | 0 | 0 | 0.3 | 0
| 2 | 100 | 4235 | 0 | 3 | N-1 | 9.74 | 8.54 | N2 | 9.7537 | 8.529 | N1 | 9.7411 | 8.5365 | N | 11.4935 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 24379.13 | 2 | 4 | N-1 | 4.73 | 1.26 | N2 | 4.9963 | 0.41721 | N1 | 4.7271 | 1.2629 | N | 5.3111 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 23654.82 | 1 | 1 | N-0 | 2.54 | 11.35 | N2 | 3.3239 | 1.0303 | N1 | 2.6076 | 11.3505 | N | 2.5388 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 23817.12 | 2 | 2 | N-1 | 7.18 | 10.67 | N2 | 7.305 | 2.3893 | N1 | 7.1781 | 10.6702 | N | 11.0776 | 197.4535 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 23684.62 | 0 | 2 | N-1 | 3.33 | 3.43 | N2 | 3.414 | 0.74876 | N1 | 3.3291 | 3.4257 | N | 4.4092 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 4235 | 2 | 2 | N-0 | 1.74 | 23.29 | N2 | 1.8739 | 2.9978 | N1 | 1.745 | 23.2903 | N | 1.7449 | 23.2903 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 15 | 4235 | 2 | 2 | N-1 | 2.63 | 27.6 | N2 | 2.7883 | 5.6209 | N1 | 2.6346 | 27.5951 | N | 2.6348 | 43.6692 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 10 | 10 | 27654.88 | 2 | 2 | N-1 | 2.22 | 0.85 | N2 | 2.2379 | 0.85392 | N1 | 2.2155 | 0.85434 | N | 3.847 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 24100.96 | 2 | 1 | N-1 | 12.31 | 11.85 | N2 | 14.7088 | 1.6117 | N1 | 12.3098 | 11.846 | N | 13.2998 | 128.9274 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 22 | 24100.96 | 0 | 1 | N-1 | 8.69 | 1.19 | N2 | 10.1262 | 2.4 | N1 | 8.6949 | 1.1914 | N | 9.6667 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 26095.45 | 4 | 5 | N-1 | 30.6 | 4.94 | N2 | 30.9426 | 4.0565 | N1 | 30.6025 | 4.9378 | N | 38.1759 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 24676.98 | 0 | 1 | N-1 | 3.24 | 3.44 | N2 | 3.8554 | 0.6753 | N1 | 3.2427 | 3.4388 | N | 3.7905 | 47.103 | 0 | 0 | 0 | 0 | 0.3 | 0
| 15 | 47.75 | 25461.36 | 3 | 6 | N-1 | 7.82 | 2.47 | N2 | 8.1434 | 2.2555 | N1 | 7.8242 | 2.4742 | N | 7.9097 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 26716.35 | 0 | 2 | N-1 | 2 | 3.35 | N2 | 2.1252 | 1.0409 | N1 | 2.0023 | 3.3518 | N | 2.0791 | 8.2264 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 24050.14 | 3 | 3 | N-1 | 2.82 | 3.7 | N2 | 2.8653 | 2.5336 | N1 | 2.8224 | 3.6976 | N | 3.0639 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 24050.14 | 3 | 3 | N-0 | 3.13 | 1.87 | N2 | 3.3585 | 0.33407 | N1 | 3.1301 | 1.8693 | N | 3.13 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 24050.14 | 0 | 2 | N-1 | 4.78 | 3.75 | N2 | 4.9373 | 1.1486 | N1 | 4.7839 | 3.7453 | N | 6.5666 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 23681.67 | 2 | 3 | N-1 | 4.52 | 4.17 | N2 | 4.9471 | 0.76504 | N1 | 4.5155 | 4.1672 | N | 4.519 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 27702.32 | 4 | 3 | N-1 | 31.99 | 18.5 | N2 | 32.0198 | 18.4931 | N1 | 31.9924 | 18.5001 | N | 76.8396 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 26383.55 | 2 | 1 | N-1 | 2.75 | 0.59 | N2 | 3.1649 | 1.3797 | N1 | 2.7502 | 0.58712 | N | 3.723 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 24882.67 | 2 | 2 | N-1 | 5.55 | 6.98 | N2 | 5.669 | 1.4173 | N1 | 5.5527 | 6.985 | N | 7.8509 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 24159.21 | 0 | 1 | N-0 | 0.61 | 4.23 | N2 | 0.75814 | 1.0014 | N1 | 0.63381 | 4.2311 | N | 0.61394 | 4.2311 | 0 | 0 | 0 | 0 | 0 | 0
| 25 | 20 | 24822.17 | 0 | 2 | N-1 | 3.12 | 3 | N2 | 3.2016 | 0.60933 | N1 | 3.1219 | 2.9986 | N | 4.0083 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 24822.17 | 2 | 2 | N-1 | 3.08 | 5.1 | N2 | 3.1492 | 1.9907 | N1 | 3.0831 | 5.1027 | N | 3.5051 | 31.7154 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 30.77 | 24305.03 | 2 | 2 | N-1 | 4.35 | 4.77 | N2 | 4.4577 | 0.93808 | N1 | 4.3483 | 4.771 | N | 5.7536 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 4235 | 2 | 2 | N-1 | 6.62 | 11.49 | N2 | 6.7602 | 4.2248 | N1 | 6.6161 | 11.487 | N | 6.9671 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 24102.68 | 2 | 3 | N-1 | 2.04 | 3.5 | N2 | 2.1611 | 1.2452 | N1 | 2.038 | 3.504 | N | 2.1345 | 10.3845 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 25678.23 | 3 | 2 | N-1 | 7.96 | 6.72 | N2 | 8.1578 | 1.2726 | N1 | 7.9615 | 6.7152 | N | 9.8765 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 25447.15 | 2 | 2 | N-1 | 3.82 | 3.87 | N2 | 3.9187 | 0.68975 | N1 | 3.8207 | 3.8736 | N | 4.845 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 22994.18 | 0 | 1 | N-1 | 1.47 | 2.15 | N2 | 1.8095 | 0.31845 | N1 | 1.4672 | 2.1538 | N | 1.506 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 26845 | 0 | 1 | N-1 | 1.56 | 2.95 | N2 | 1.881 | 1.3911 | N1 | 1.5644 | 2.9524 | N | 1.6785 | 15.4837 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 28454.8 | 2 | 4 | N-1 | 65.66 | 57.28 | N2 | 75.6877 | 1.0828 | N1 | 65.6562 | 57.2802 | N | 65.7211 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 26845 | 0 | 1 | N-1 | 1.55 | 2.11 | N2 | 1.8091 | 2.2043 | N1 | 1.5495 | 2.1133 | N | 1.5734 | 13.2034 | 0 | 0 | 0 | 0 | 0.1 | 0
| 37 | 141.89 | 27404.59 | 2 | 2 | N-1 | 4.32 | 4.55 | N2 | 4.4105 | 3.3444 | N1 | 4.3232 | 4.5481 | N | 5.317 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 23973.32 | 2 | 3 | N-1 | 5.07 | 8.66 | N2 | 5.4642 | 1.7351 | N1 | 5.0674 | 8.6578 | N | 5.1597 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 24285.1 | 2 | 5 | N-1 | 4.71 | 8.07 | N2 | 5.0665 | 1.1338 | N1 | 4.7112 | 8.0671 | N | 4.7215 | 10.5275 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 40 | 47.51 | 24599.75 | 3 | 3 | N-1 | 6.27 | 7.46 | N2 | 6.4524 | 1.547 | N1 | 6.2659 | 7.4603 | N | 6.4668 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 28147.91 | 0 | 6 | N-1 | 4.96 | 1.82 | N2 | 4.966 | 1.82 | N1 | 4.9562 | 1.8246 | N | 5.4012 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 25202.28 | 2 | 2 | N-1 | 10.21 | 17.23 | N2 | 10.2919 | 2.8252 | N1 | 10.2064 | 17.2288 | N | 14.9097 | 233.451 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 43 | 372.81 | 25430.98 | 3 | 2 | N-1 | 8.18 | 20.61 | N2 | 8.2731 | 4.8349 | N1 | 8.1792 | 20.6133 | N | 8.6367 | 46.0638 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 44 | 162 | 26155.14 | 1 | 2 | N-2 | 4.8 | 0.96 | N2 | 4.8023 | 0.95816 | N1 | 4.9567 | 7.4825 | N | 6.2568 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 26155.14 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.8023 | 0.95816 | N1 | 4.1262 | 0.59124 | N | 5.1807 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 24655.99 | 0 | 2 | N-1 | 1.76 | 2.88 | N2 | 1.8075 | 1.556 | N1 | 1.7626 | 2.8782 | N | 2.1386 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 23772.68 | 0 | 2 | N-1 | 2.11 | 0.69 | N2 | 2.1242 | 0.68598 | N1 | 2.1141 | 0.68633 | N | 3.1472 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 25805.29 | 1 | 6 | N-1 | 12.98 | 9.26 | N2 | 13.8421 | 0.95152 | N1 | 12.9847 | 9.2616 | N | 14.2062 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 22523.52 | 1 | 3 | N-1 | 1.32 | 2.17 | N2 | 1.4138 | 0.59335 | N1 | 1.3213 | 2.1674 | N | 1.335 | 4.884 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 26002.69 | 2 | 2 | N-1 | 4.03 | 0.82 | N2 | 4.0593 | 0.8243 | N1 | 4.028 | 0.8247 | N | 5.2875 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 26845 | 0 | 1 | N-1 | 1.33 | 1.77 | N2 | 1.6022 | 1.5594 | N1 | 1.3261 | 1.7704 | N | 1.392 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 26881.03 | 2 | 3 | N-1 | 5.74 | 5.85 | N2 | 6.0866 | 0.43613 | N1 | 5.7369 | 5.851 | N | 6.2914 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 24017.74 | 0 | 1 | N-1 | 2.79 | 2.23 | N2 | 3.2638 | 0.42251 | N1 | 2.7862 | 2.2316 | N | 3.0532 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 24871.17 | 1 | 2 | N-1 | 9.95 | 14.48 | N2 | 10.1232 | 1.4126 | N1 | 9.9528 | 14.4819 | N | 11.8126 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 24871.17 | 2 | 2 | N-1 | 10.37 | 9.96 | N2 | 10.6192 | 1.461 | N1 | 10.3673 | 9.9648 | N | 12.3508 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 27975.16 | 2 | 1 | N-0 | 0.58 | 1.27 | N2 | 0.77739 | 0.10523 | N1 | 0.5973 | 1.0556 | N | 0.58263 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 20519.55 | 0 | 1 | N-0 | 0.99 | 6.87 | N2 | 1.231 | 0.76487 | N1 | 1.0159 | 6.8747 | N | 0.98768 | 6.8747 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 24262.96 | 2 | 2 | N-1 | 4.77 | 5.5 | N2 | 4.8845 | 1.0842 | N1 | 4.7705 | 5.5017 | N | 6.42 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 28147.91 | 2 | 2 | N-1 | 15.77 | 4.07 | N2 | 15.8661 | 4.0714 | N1 | 15.7736 | 4.0722 | N | 24.7932 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 23642.64 | 2 | 2 | N-1 | 1.46 | 2.5 | N2 | 1.5379 | 1.3437 | N1 | 1.4616 | 2.4993 | N | 1.5872 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 25259.08 | 2 | 3 | N-1 | 6.12 | 6.1 | N2 | 6.3651 | 0.85962 | N1 | 6.1185 | 6.0966 | N | 7.3162 | 69.2747 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 62 | 424.67 | 27654.88 | 3 | 6 | N-1 | 31.62 | 2.71 | N2 | 32.766 | 0.99624 | N1 | 31.6158 | 2.7119 | N | 32.7648 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 24056.5 | 3 | 2 | N-1 | 11.96 | 7.74 | N2 | 11.9804 | 7.7353 | N1 | 11.9641 | 7.7367 | N | 28.1593 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 24056.5 | 3 | 5 | N-1 | 7.53 | 1.06 | N2 | 7.772 | 0.46723 | N1 | 7.5279 | 1.0615 | N | 8.0323 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 24481.12 | 2 | 2 | N-1 | 6.57 | 6.01 | N2 | 6.6345 | 2.2345 | N1 | 6.5741 | 6.0093 | N | 10.3002 | 184.6689 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 66 | 29.15 | 4235 | 0 | 3 | N-1 | 4.47 | 3.35 | N2 | 4.4831 | 3.3477 | N1 | 4.4726 | 3.3507 | N | 5.0735 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 23950.37 | 2 | 3 | N-1 | 4.16 | 8.29 | N2 | 4.4548 | 1.5413 | N1 | 4.1566 | 8.2898 | N | 4.2168 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 24535.64 | 3 | 3 | N-1 | 6.9 | 6.39 | N2 | 7.0864 | 0.60106 | N1 | 6.897 | 6.3925 | N | 7.4986 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 22929.08 | 2 | 1 | N-1 | 6.07 | 7.18 | N2 | 7.0171 | 1.7985 | N1 | 6.0695 | 7.1819 | N | 7.643 | 119.458 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 23765.75 | 0 | 2 | N-1 | 1.61 | 2.9 | N2 | 1.6609 | 2.1544 | N1 | 1.6068 | 2.899 | N | 1.8306 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 25442.16 | 2 | 2 | N-1 | 16.64 | 31.58 | N2 | 17.3364 | 1.4226 | N1 | 16.6404 | 31.5849 | N | 17.4705 | 82.1605 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 31184.26 | 0 | 1 | N-1 | 1.7 | 2.65 | N2 | 2.0351 | 0.7478 | N1 | 1.6974 | 2.6538 | N | 1.7346 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 23072.06 | 0 | 3 | N-0 | 4.57 | 4.28 | N2 | 4.8623 | 0.61406 | N1 | 4.57 | 4.2811 | N | 4.57 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 25866.13 | 4 | 2 | N-1 | 10.72 | 3.19 | N2 | 10.7192 | 3.1938 | N1 | 10.717 | 3.1945 | N | 16.8489 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 26973.94 | 5 | 9 | N-1 | 24.19 | 7.56 | N2 | 24.3052 | 1.1185 | N1 | 24.1891 | 7.5573 | N | 25.3032 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 25374.68 | 2 | 2 | N-1 | 9.39 | 15.51 | N2 | 9.4822 | 2.7746 | N1 | 9.3904 | 15.514 | N | 14.1222 | 229.282 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 80 | 24 | 24434.23 | 2 | 3 | N-1 | 3.96 | 5.92 | N2 | 4.2931 | 1.202 | N1 | 3.9643 | 5.9183 | N | 4.023 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 24434.23 | 2 | 3 | N-1 | 6.35 | 11.27 | N2 | 6.6285 | 0.68442 | N1 | 6.3489 | 11.2735 | N | 7.1538 | 55.1908 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 82 | 4.89 | 23723.98 | 2 | 2 | N-1 | 1.37 | 2.95 | N2 | 1.414 | 1.8897 | N1 | 1.3741 | 2.9473 | N | 1.5714 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 27654.88 | 3 | 4 | N-1 | 19.12 | 32.5 | N2 | 19.13 | 32.4807 | N1 | 19.1159 | 32.4984 | N | 97.7676 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 4235.09 | 4 | 4 | N-1 | 48.18 | 155.19 | N2 | 48.3314 | 155.1076 | N1 | 48.184 | 155.1895 | N | 102.5189 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 24871.17 | 2 | 2 | N-1 | 13.46 | 15.24 | N2 | 13.7377 | 2.6094 | N1 | 13.4635 | 15.2431 | N | 17.471 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 23798.04 | 2 | 2 | N-1 | 4.52 | 7.21 | N2 | 4.5919 | 1.3712 | N1 | 4.5229 | 7.2129 | N | 6.677 | 113.3242 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 87 | 98.91 | 24871.17 | 2 | 4 | N-1 | 10.87 | 17.75 | N2 | 11.6502 | 1.6868 | N1 | 10.874 | 17.7462 | N | 10.9848 | 27.6312 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 24882.51 | 3 | 2 | N-1 | 24.66 | 60.18 | N2 | 25.2432 | 5.1891 | N1 | 24.6605 | 60.1784 | N | 24.9347 | 96.7024 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 72.49 | 24389.08 | 3 | 4 | N-1 | 8.9 | 12.36 | N2 | 9.2693 | 2.7719 | N1 | 8.8978 | 12.3577 | N | 9.0335 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 24389.08 | 0 | 2 | N-1 | 6.01 | 2.76 | N2 | 6.0203 | 2.7591 | N1 | 6.0082 | 2.7596 | N | 11.5732 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 24389.08 | 1 | 3 | N-1 | 3.6 | 4.09 | N2 | 3.8749 | 1.2593 | N1 | 3.601 | 4.0889 | N | 3.641 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 23859.21 | 2 | 4 | N-0 | 9.23 | 11.88 | N2 | 10.0924 | 1.914 | N1 | 9.2287 | 11.8764 | N | 9.2287 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 23859.21 | 2 | 4 | N-0 | 1.25 | 0.85 | N2 | 1.3971 | 0.10098 | N1 | 1.2511 | 0.84687 | N | 1.251 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 27654.88 | 2 | 2 | N-1 | 14.68 | 2.55 | N2 | 14.7705 | 2.55 | N1 | 14.6837 | 2.5513 | N | 18.8537 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 24322.82 | 2 | 2 | N-1 | 12.86 | 5.84 | N2 | 12.9389 | 5.8401 | N1 | 12.8625 | 5.8412 | N | 24.7496 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 24322.82 | 0 | 1 | N-0 | 1.5 | 4.99 | N2 | 1.9868 | 0.36562 | N1 | 1.5423 | 4.9655 | N | 1.5015 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 26095.45 | 2 | 4 | N-1 | 16.3 | 6.18 | N2 | 17.1119 | 2.3893 | N1 | 16.2959 | 6.1822 | N | 20.9422 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 25139.86 | 2 | 4 | N-1 | 5.84 | 8.86 | N2 | 6.2947 | 1.9882 | N1 | 5.8432 | 8.8597 | N | 5.9631 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 22806.36 | 0 | 2 | N-1 | 2.42 | 2.56 | N2 | 2.4325 | 2.5593 | N1 | 2.4223 | 2.5608 | N | 2.567 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 22806.36 | 2 | 6 | N-1 | 3.21 | 3.52 | N2 | 3.4865 | 0.74557 | N1 | 3.2102 | 3.5196 | N | 3.2133 | 6.2109 | 0 | 0.5 | 0 | 0 | 0.1 | 0

## oq25VCR130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 46954 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 7865 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 45276 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 43930 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 44232 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 43986 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 7865 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 7865 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 51359 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 44759 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 44759 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 48463 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 45829 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 47285 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 49616 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 44665 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 44665 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 44665 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 43980 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 51447 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 48998 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 46211 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 44867 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 46098 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 46098 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 45138 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 7865 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 44762 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 47688 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 47259 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 42703 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 49855 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 52845 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 49855 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 50894 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 44522 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 45101 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 45685 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 52275 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 46804 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 47229 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 48574 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 48574 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 45790 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 44149 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 47924 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 41829 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 48291 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 49855 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 49922 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 44604 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 46189 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 46189 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 51954 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 38108 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 45060 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 52275 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 43908 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 46910 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 51359 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 44676 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 44676 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 45465 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 7865 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 44479 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 45566 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 42583 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 44136 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 47250 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 57914 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 42848 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 48037 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 50094 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 47124 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 45378 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 45378 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 44059 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 51359 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 7865 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 46189 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 44196 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 46189 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 46210 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 45294 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 45294 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 45294 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 44310 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 44310 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 51359 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 45171 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 45171 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 48463 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 46688 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 42355 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 42355 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 46954.21 | 0 | 3 | N-1 | 10.43 | 0.7 | N2 | 10.4479 | 0.69847 | N1 | 10.4349 | 0.69908 | N | 11.8869 | 49.968 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 100 | 7865 | 0 | 3 | N-1 | 9.77 | 6.59 | N2 | 9.7796 | 6.5904 | N1 | 9.767 | 6.593 | N | 13.719 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 45275.52 | 2 | 4 | N-1 | 4.75 | 1.26 | N2 | 5.005 | 0.41721 | N1 | 4.7535 | 1.2629 | N | 6.1279 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 43930.38 | 1 | 1 | N-1 | 2.73 | 2.8 | N2 | 3.3448 | 1.0303 | N1 | 2.7315 | 2.8048 | N | 2.769 | 11.3505 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.68 | 0.27 | N2 | 32.6654 | 0.5367 | N1 | 28.6837 | 0.27224 | N | 53.3389 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 44231.79 | 2 | 2 | N-1 | 7.3 | 2.09 | N2 | 7.3506 | 2.0877 | N1 | 7.3032 | 2.088 | N | 15.1085 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 43985.72 | 0 | 2 | N-1 | 3.4 | 3.43 | N2 | 3.4292 | 0.74876 | N1 | 3.3986 | 3.4257 | N | 5.6582 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 7865 | 2 | 2 | N-1 | 1.79 | 7.55 | N2 | 1.8847 | 2.8772 | N1 | 1.7938 | 7.5519 | N | 1.8295 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 7865 | 2 | 2 | N-1 | 2.69 | 14.16 | N2 | 2.8085 | 5.3948 | N1 | 2.6891 | 14.1599 | N | 2.7933 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 51359.06 | 2 | 2 | N-1 | 2.24 | 0.85 | N2 | 2.2581 | 0.85392 | N1 | 2.2357 | 0.85434 | N | 5.52 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 44758.93 | 2 | 1 | N-1 | 12.45 | 3.98 | N2 | 14.7395 | 1.2499 | N1 | 12.4523 | 3.9777 | N | 15.9632 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 44758.93 | 0 | 1 | N-1 | 8.72 | 1.19 | N2 | 10.1758 | 2.4 | N1 | 8.7195 | 1.1914 | N | 12.0294 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 48462.97 | 4 | 5 | N-1 | 30.71 | 4.94 | N2 | 31.0333 | 4.0565 | N1 | 30.713 | 4.9378 | N | 46.0829 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 45828.67 | 0 | 1 | N-1 | 3.29 | 1.41 | N2 | 3.8697 | 0.6753 | N1 | 3.2873 | 1.4112 | N | 4.7869 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 47285.39 | 3 | 6 | N-1 | 7.86 | 0.6 | N2 | 8.1699 | 0.21598 | N1 | 7.8596 | 0.60435 | N | 8.3004 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 49616.08 | 0 | 2 | N-1 | 2.06 | 2.13 | N2 | 2.149 | 1.0409 | N1 | 2.0641 | 2.1305 | N | 2.2675 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 44664.55 | 3 | 3 | N-1 | 2.87 | 0.28 | N2 | 2.889 | 0.28383 | N1 | 2.8675 | 0.28407 | N | 3.4806 | 20.21 | 0 | 0.1 | 0 | 0 | 0 | 0
| 18 | 17.25 | 44664.55 | 3 | 3 | N-0 | 3.17 | 1.87 | N2 | 3.3641 | 0.25637 | N1 | 3.1686 | 1.8693 | N | 3.1685 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 44664.55 | 0 | 2 | N-1 | 4.86 | 3.75 | N2 | 4.961 | 1.1486 | N1 | 4.8611 | 3.7453 | N | 8.5121 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 43980.24 | 2 | 3 | N-1 | 4.6 | 4.17 | N2 | 4.9627 | 0.71472 | N1 | 4.6001 | 4.1672 | N | 4.6441 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 51447.17 | 4 | 3 | N-1 | 32.43 | 18.5 | N2 | 32.459 | 18.4931 | N1 | 32.4317 | 18.5001 | N | 117.7537 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 48998.02 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1959 | 1.2056 | N1 | 2.7635 | 0.58712 | N | 5.0614 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 46210.67 | 2 | 2 | N-1 | 5.66 | 1.42 | N2 | 5.6993 | 1.4173 | N1 | 5.6601 | 1.418 | N | 10.3489 | 117.1216 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 1.96 | 44867.1 | 0 | 1 | N-1 | 0.65 | 0.72 | N2 | 0.77888 | 1.0014 | N1 | 0.65227 | 0.72302 | N | 0.70156 | 4.2311 | 0 | 0 | 0 | 0 | 0.1 | 0
| 25 | 20 | 46098.32 | 0 | 2 | N-1 | 3.19 | 3 | N2 | 3.2146 | 0.60933 | N1 | 3.1857 | 2.9986 | N | 5.0735 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 46098.32 | 2 | 2 | N-1 | 3.13 | 0.38 | N2 | 3.1578 | 0.38384 | N1 | 3.1309 | 0.38403 | N | 4.1799 | 31.7154 | 0 | 0.1 | 0 | 0 | 0 | 0
| 27 | 30.77 | 45137.91 | 2 | 2 | N-1 | 4.44 | 0.94 | N2 | 4.4772 | 0.93808 | N1 | 4.444 | 0.93854 | N | 7.3685 | 77.5201 | 0 | 0.1 | 0 | 0 | 0 | 0
| 28 | 60 | 7865 | 2 | 2 | N-1 | 6.65 | 6.79 | N2 | 6.7722 | 2.9632 | N1 | 6.646 | 6.7941 | N | 7.8561 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 44762.12 | 2 | 3 | N-1 | 2.09 | 2.09 | N2 | 2.1868 | 1.2452 | N1 | 2.0933 | 2.0923 | N | 2.3491 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 47688.14 | 3 | 2 | N-1 | 8.11 | 6.72 | N2 | 8.1858 | 1.2726 | N1 | 8.1093 | 6.7152 | N | 12.1885 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 47259 | 2 | 2 | N-1 | 3.9 | 0.69 | N2 | 3.9337 | 0.68975 | N1 | 3.9031 | 0.69009 | N | 6.0883 | 56.997 | 0 | 0.1 | 0 | 0 | 0 | 0
| 32 | 8.41 | 42703.47 | 0 | 1 | N-1 | 1.51 | 2.15 | N2 | 1.8145 | 0.24519 | N1 | 1.5096 | 2.1538 | N | 1.7191 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.22 | N2 | 37.3282 | 0.30895 | N1 | 32.7887 | 0.21612 | N | 57.0299 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 49855 | 0 | 1 | N-1 | 1.61 | 0.45 | N2 | 1.8953 | 0.26409 | N1 | 1.6079 | 0.45 | N | 2.0348 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 52844.62 | 2 | 4 | N-1 | 67.05 | 57.28 | N2 | 75.7141 | 1.0828 | N1 | 67.0533 | 57.2802 | N | 67.3714 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 49855 | 0 | 1 | N-1 | 1.58 | 0.83 | N2 | 1.8296 | 0.21218 | N1 | 1.581 | 0.82521 | N | 1.8772 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 50894.23 | 2 | 2 | N-1 | 4.4 | 0.6 | N2 | 4.4268 | 0.60246 | N1 | 4.4019 | 0.60258 | N | 6.5379 | 51.9745 | 0 | 0.1 | 0 | 0 | 0 | 0
| 38 | 35.04 | 44521.87 | 2 | 3 | N-1 | 5.21 | 5.31 | N2 | 5.4955 | 0.90063 | N1 | 5.215 | 5.3129 | N | 5.4574 | 14.485 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 39 | 23.76 | 45100.89 | 2 | 5 | N-1 | 4.76 | 1.56 | N2 | 5.0897 | 1.1034 | N1 | 4.7566 | 1.5584 | N | 4.9407 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 45685.26 | 3 | 3 | N-1 | 6.4 | 5.38 | N2 | 6.4706 | 0.33551 | N1 | 6.3979 | 5.3837 | N | 6.9689 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 52274.68 | 0 | 6 | N-1 | 4.97 | 0.29 | N2 | 4.9763 | 0.2877 | N1 | 4.9664 | 0.28796 | N | 6.0189 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 46804.23 | 2 | 2 | N-1 | 10.29 | 2.47 | N2 | 10.3483 | 2.4682 | N1 | 10.2855 | 2.4687 | N | 19.9527 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 47228.97 | 3 | 2 | N-1 | 8.32 | 0.86 | N2 | 8.3248 | 0.8618 | N1 | 8.3231 | 0.86207 | N | 9.6408 | 46.0638 | 0 | 0 | 0 | 0 | 0 | 0
| 44 | 162 | 48573.84 | 1 | 2 | N-2 | 4.82 | 0.96 | N2 | 4.8238 | 0.95816 | N1 | 5.048 | 0.7577 | N | 8.0401 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 48573.84 | 1 | 1 | N-1 | 4.14 | 0.59 | N2 | 4.8238 | 0.95816 | N1 | 4.1395 | 0.59124 | N | 6.6063 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 45789.7 | 0 | 2 | N-1 | 1.8 | 0.8 | N2 | 1.8211 | 0.29539 | N1 | 1.8044 | 0.79952 | N | 2.6516 | 24.2723 | 0 | 0 | 0 | 0 | 0.1 | 0
| 47 | 10.2 | 44149.26 | 0 | 2 | N-1 | 2.13 | 0.69 | N2 | 2.1382 | 0.68598 | N1 | 2.1281 | 0.68633 | N | 4.2958 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 47924.11 | 1 | 6 | N-1 | 13.19 | 9.26 | N2 | 13.8631 | 0.95152 | N1 | 13.1896 | 9.2616 | N | 15.9541 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 41829.4 | 1 | 3 | N-1 | 1.35 | 1.23 | N2 | 1.4253 | 0.59335 | N1 | 1.3534 | 1.2265 | N | 1.4293 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 48290.72 | 2 | 2 | N-1 | 4.05 | 0.82 | N2 | 4.0777 | 0.8243 | N1 | 4.0464 | 0.8247 | N | 6.8057 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 49855 | 0 | 1 | N-1 | 1.36 | 1.08 | N2 | 1.6304 | 0.79071 | N1 | 1.3635 | 1.0849 | N | 1.6535 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 49921.91 | 2 | 3 | N-1 | 5.86 | 0.57 | N2 | 6.0966 | 0.43613 | N1 | 5.8633 | 0.57173 | N | 7.1178 | 35.8672 | 0 | 0.2 | 0 | 0 | 0 | 0
| 53 | 20.68 | 44604.37 | 0 | 1 | N-1 | 2.83 | 2.23 | N2 | 3.2725 | 0.42251 | N1 | 2.8321 | 2.2316 | N | 3.7678 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 46189.31 | 1 | 2 | N-2 | 10.15 | 1.41 | N2 | 10.1533 | 1.4126 | N1 | 10.179 | 3.5333 | N | 14.3406 | 118.5846 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 46189.31 | 2 | 2 | N-1 | 10.58 | 9.96 | N2 | 10.6503 | 1.461 | N1 | 10.5797 | 9.9648 | N | 14.9233 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 51953.87 | 2 | 1 | N-0 | 0.61 | 1.27 | N2 | 0.77991 | 0.10523 | N1 | 0.62261 | 1.0556 | N | 0.61313 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 38107.73 | 0 | 1 | N-1 | 1.06 | 1.61 | N2 | 1.2445 | 0.76487 | N1 | 1.0582 | 1.6136 | N | 1.1086 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 45059.79 | 2 | 2 | N-1 | 4.87 | 1.08 | N2 | 4.907 | 1.0842 | N1 | 4.8717 | 1.0847 | N | 8.2834 | 89.5966 | 0 | 0.1 | 0 | 0 | 0 | 0
| 59 | 227.28 | 52274.68 | 2 | 2 | N-1 | 15.87 | 4.07 | N2 | 15.9644 | 4.0714 | N1 | 15.8719 | 4.0722 | N | 34.084 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 43907.77 | 2 | 2 | N-1 | 1.51 | 1.69 | N2 | 1.5651 | 1.3437 | N1 | 1.5088 | 1.6852 | N | 1.8076 | 10.8753 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 61 | 44.01 | 46909.72 | 2 | 3 | N-1 | 6.15 | 0.96 | N2 | 6.382 | 0.75361 | N1 | 6.1472 | 0.95635 | N | 8.816 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 51359.06 | 3 | 6 | N-1 | 31.68 | 2.71 | N2 | 32.7897 | 0.99624 | N1 | 31.6801 | 2.7119 | N | 34.9564 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 44676.36 | 3 | 2 | N-1 | 12.12 | 7.74 | N2 | 12.14 | 7.7353 | N1 | 12.1236 | 7.7367 | N | 43.3412 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 44676.36 | 3 | 5 | N-1 | 7.55 | 0.83 | N2 | 7.7816 | 0.46723 | N1 | 7.5477 | 0.82782 | N | 8.8468 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 45464.93 | 2 | 2 | N-1 | 6.63 | 1.95 | N2 | 6.6784 | 1.9525 | N1 | 6.6344 | 1.9529 | N | 14.1753 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 7865 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4953 | 3.3477 | N1 | 4.4848 | 3.3507 | N | 5.947 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 44479.26 | 2 | 3 | N-1 | 4.31 | 0.87 | N2 | 4.4856 | 1.4824 | N1 | 4.309 | 0.87157 | N | 4.4728 | 12.4713 | 0 | 0.2 | 0 | 0 | 0 | 0
| 68 | 54.9 | 45566.19 | 3 | 3 | N-1 | 7.03 | 6.39 | N2 | 7.0991 | 0.60106 | N1 | 7.0314 | 6.3925 | N | 8.3972 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 42582.58 | 2 | 1 | N-1 | 6.14 | 1.21 | N2 | 7.0525 | 1.7985 | N1 | 6.1423 | 1.2061 | N | 9.9908 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 44136.4 | 0 | 2 | N-1 | 1.65 | 1.89 | N2 | 1.6879 | 0.20738 | N1 | 1.6521 | 1.8918 | N | 2.1777 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 47249.73 | 2 | 2 | N-1 | 17.15 | 19.75 | N2 | 17.3674 | 1.4226 | N1 | 17.1499 | 19.7476 | N | 19.2622 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.19 | N2 | 27.7161 | 0.19398 | N1 | 27.716 | 0.19399 | N | 43.9822 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 57913.63 | 0 | 1 | N-1 | 1.76 | 1.46 | N2 | 2.0543 | 0.71637 | N1 | 1.7645 | 1.4641 | N | 2.0195 | 10.6592 | 0 | 0 | 0 | 0 | 0.3 | 0
| 74 | 34 | 42848.11 | 0 | 3 | N-0 | 4.65 | 4.28 | N2 | 4.8744 | 0.55576 | N1 | 4.6547 | 4.2811 | N | 4.6546 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 48037.09 | 4 | 2 | N-1 | 10.79 | 3.19 | N2 | 10.7901 | 3.1938 | N1 | 10.7879 | 3.1945 | N | 23.0591 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 50094.45 | 5 | 9 | N-1 | 24.33 | 1.12 | N2 | 24.331 | 1.1185 | N1 | 24.3297 | 1.1189 | N | 27.0721 | 76.5061 | 0 | 0 | 0 | 0 | 0 | 0
| 79 | 101.44 | 47124.4 | 2 | 2 | N-1 | 9.48 | 2.42 | N2 | 9.5375 | 2.4242 | N1 | 9.4789 | 2.4246 | N | 19.1091 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 45377.85 | 2 | 3 | N-1 | 4.08 | 3.66 | N2 | 4.3181 | 1.1597 | N1 | 4.0789 | 3.66 | N | 4.2305 | 9.9085 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 81 | 47 | 45377.85 | 2 | 3 | N-1 | 6.39 | 0.92 | N2 | 6.6424 | 0.60038 | N1 | 6.3937 | 0.91564 | N | 8.3097 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 44058.81 | 2 | 2 | N-1 | 1.42 | 1.26 | N2 | 1.4433 | 0.95993 | N1 | 1.4197 | 1.2632 | N | 1.8825 | 15.2973 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 209.66 | 51359.06 | 3 | 4 | N-1 | 19.89 | 32.5 | N2 | 19.8999 | 32.4807 | N1 | 19.8862 | 32.4984 | N | 167.211 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 7865.16 | 4 | 4 | N-1 | 48.75 | 155.19 | N2 | 48.8944 | 155.1076 | N1 | 48.7473 | 155.1895 | N | 151.9463 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 46189.31 | 2 | 2 | N-1 | 13.71 | 2.28 | N2 | 13.7927 | 2.2791 | N1 | 13.7114 | 2.2795 | N | 22.0663 | 215.5592 | 0 | 0.1 | 0 | 0 | 0 | 0
| 86 | 32.16 | 44196.35 | 2 | 2 | N-1 | 4.59 | 1.37 | N2 | 4.6199 | 1.3712 | N1 | 4.586 | 1.3719 | N | 8.9887 | 113.3242 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 46189.31 | 2 | 4 | N-1 | 11.04 | 0.85 | N2 | 11.6657 | 0.30116 | N1 | 11.0431 | 0.84904 | N | 11.5738 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 46210.38 | 3 | 2 | N-1 | 25.26 | 1.68 | N2 | 25.2949 | 1.6818 | N1 | 25.2629 | 1.683 | N | 26.9971 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 45294 | 3 | 4 | N-1 | 9.1 | 0.58 | N2 | 9.2899 | 0.29643 | N1 | 9.1046 | 0.57925 | N | 9.5047 | 22.5424 | 0 | 0.1 | 0 | 0 | 0 | 0
| 90 | 54.2 | 45294 | 0 | 2 | N-1 | 6.07 | 2.76 | N2 | 6.078 | 2.7591 | N1 | 6.0659 | 2.7596 | N | 17.0229 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 45294 | 1 | 3 | N-1 | 3.69 | 4.09 | N2 | 3.9012 | 1.2593 | N1 | 3.6864 | 4.0889 | N | 3.8623 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 44309.96 | 2 | 4 | N-0 | 9.47 | 11.88 | N2 | 10.1234 | 1.4548 | N1 | 9.4716 | 11.8764 | N | 9.4716 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 44309.96 | 2 | 4 | N-0 | 1.27 | 0.85 | N2 | 1.3992 | 0.10098 | N1 | 1.2684 | 0.84687 | N | 1.2683 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 51359.06 | 2 | 2 | N-1 | 14.74 | 2.23 | N2 | 14.8298 | 2.2272 | N1 | 14.743 | 2.2276 | N | 23.847 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 45170.95 | 2 | 2 | N-1 | 12.98 | 5.84 | N2 | 13.0607 | 5.8401 | N1 | 12.9843 | 5.8412 | N | 36.2654 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 45170.95 | 0 | 1 | N-0 | 1.61 | 4.99 | N2 | 1.9929 | 0.2836 | N1 | 1.6261 | 1.5589 | N | 1.6056 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 48462.97 | 2 | 4 | N-1 | 16.43 | 6.18 | N2 | 17.1654 | 2.3893 | N1 | 16.4341 | 6.1822 | N | 25.9336 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 46688.32 | 2 | 4 | N-1 | 5.97 | 1.21 | N2 | 6.3246 | 1.0064 | N1 | 5.9735 | 1.2096 | N | 6.3223 | 16.6658 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 42354.66 | 0 | 2 | N-1 | 2.44 | 0.25 | N2 | 2.4541 | 0.24635 | N1 | 2.4439 | 0.24648 | N | 2.9627 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 42354.66 | 2 | 6 | N-1 | 3.24 | 1.07 | N2 | 3.4921 | 0.07716 | N1 | 3.2433 | 1.072 | N | 3.3347 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25length70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 105 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 105 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 105 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 210 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 11 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 105 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 105 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 105 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 105 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 105 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 210 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 210 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 105 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 105 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 105 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 105 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 105 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 105 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 105 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 105 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 105 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 105 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 105 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 105 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 105 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 105 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 105 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 105 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 105 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 105 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 105 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 105 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 11 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 105 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 21 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 105 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 21 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 105 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 105 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 105 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 105 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 105 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 21 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 21 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 21 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 105 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 105 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 105 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 105 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 105 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 105 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 105 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 105 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 105 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 105 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 105 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 105 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 105 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 105 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 105 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 105 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 105 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 105 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 105 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 105 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 105 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 105 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 105 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 105 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 105 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 105 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 11 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 105 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 105 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 21 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 11 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 11 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 21 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 105 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 105 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 105 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 105 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 105 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 105 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 105 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 105 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 105 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 105 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 105 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 105 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 105 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 105 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 105 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 105 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 105 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 105 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 105 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 105 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 105 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 105 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 7.29 | 8.46 | N2 | 7.3288 | 0.45048 | N1 | 7.2869 | 8.455 | N | 7.9413 | 34.8745 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 6.85 | 5.52 | N2 | 6.8575 | 5.5122 | N1 | 6.8513 | 5.5159 | N | 8.8227 | 428.3722 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 3.41 | 1.05 | N2 | 3.5893 | 0.29827 | N1 | 3.413 | 1.0522 | N | 4.0969 | 28.1802 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 1.88 | 8.01 | N2 | 2.3534 | 0.71703 | N1 | 1.9234 | 1.9747 | N | 1.8845 | 8.0095 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 20.93 | 0.23 | N2 | 23.7072 | 0.43926 | N1 | 20.935 | 0.22815 | N | 39.138 | 243.3683 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 5.24 | 1.62 | N2 | 5.2749 | 1.6238 | N1 | 5.2428 | 1.6244 | N | 9.357 | 140.2904 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 2.38 | 2.39 | N2 | 2.4156 | 0.50107 | N1 | 2.3803 | 2.3929 | N | 3.5248 | 43.0284 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.28 | 5.35 | N2 | 1.3471 | 2.0771 | N1 | 1.2813 | 5.3498 | N | 1.2837 | 16.5476 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 1.92 | 10.03 | N2 | 2.0059 | 3.8946 | N1 | 1.9154 | 10.0309 | N | 1.9486 | 31.0268 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 1.62 | 0.58 | N2 | 1.6311 | 0.58037 | N1 | 1.6163 | 0.58058 | N | 3.3435 | 50.1463 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 8.86 | 2.8 | N2 | 10.4558 | 1.0494 | N1 | 8.8623 | 2.804 | N | 10.3904 | 90.9058 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 6.13 | 0.83 | N2 | 7.13 | 2.0072 | N1 | 6.131 | 0.83397 | N | 7.5978 | 80.0612 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 22.01 | 3.77 | N2 | 22.2153 | 2.9385 | N1 | 22.0146 | 3.7673 | N | 30.1571 | 252.0804 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 2.32 | 0.99 | N2 | 2.7244 | 0.45189 | N1 | 2.3175 | 0.98784 | N | 3.005 | 32.9721 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 5.61 | 1.81 | N2 | 5.8268 | 1.5705 | N1 | 5.6096 | 1.8074 | N | 5.8028 | 13.1387 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 1.43 | 1.49 | N2 | 1.4962 | 0.72524 | N1 | 1.4325 | 1.4893 | N | 1.5235 | 5.7525 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.05 | 2.61 | N2 | 2.0715 | 1.7697 | N1 | 2.0549 | 2.6074 | N | 2.3444 | 14.3433 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 2.26 | 1.33 | N2 | 2.41 | 0.17439 | N1 | 2.2614 | 1.3259 | N | 2.2613 | 1.3259 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 3.4 | 2.61 | N2 | 3.4847 | 0.76864 | N1 | 3.4017 | 2.614 | N | 5.2782 | 66.0025 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 3.27 | 3.12 | N2 | 3.5421 | 0.53313 | N1 | 3.272 | 3.1239 | N | 3.2881 | 4.5891 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 23.18 | 12.91 | N2 | 23.1931 | 12.9114 | N1 | 23.1797 | 12.9148 | N | 69.0415 | 1214.7404 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.01 | 0.42 | N2 | 2.2992 | 0.93768 | N1 | 2.0098 | 0.41537 | N | 3.1733 | 42.6951 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 4.06 | 4.95 | N2 | 4.0955 | 0.96319 | N1 | 4.0639 | 4.9482 | N | 6.5068 | 83.2141 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.45 | 0.51 | N2 | 0.53823 | 0.69801 | N1 | 0.45369 | 0.50612 | N | 0.46276 | 2.9618 | 0 | 0 | 0 | 0 | 0.1 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 2.23 | 2.09 | N2 | 2.2662 | 0.40775 | N1 | 2.2332 | 2.0944 | N | 3.18 | 35.0137 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 2.26 | 2.21 | N2 | 2.2812 | 1.3915 | N1 | 2.2615 | 2.2082 | N | 2.7525 | 22.5329 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 3.18 | 3.38 | N2 | 3.2232 | 0.63752 | N1 | 3.1807 | 3.3799 | N | 4.6937 | 55.0773 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 4.79 | 4.8 | N2 | 4.8727 | 2.6321 | N1 | 4.79 | 4.8002 | N | 5.3163 | 174.0088 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 1.49 | 1.51 | N2 | 1.5538 | 0.87969 | N1 | 1.4867 | 1.5084 | N | 1.6075 | 7.4756 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 5.81 | 4.72 | N2 | 5.8981 | 0.85431 | N1 | 5.81 | 4.7197 | N | 7.884 | 73.823 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 2.8 | 2.74 | N2 | 2.8352 | 0.46875 | N1 | 2.7964 | 2.7448 | N | 3.9121 | 40.4956 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.05 | 1.51 | N2 | 1.2686 | 0.20416 | N1 | 1.0467 | 1.5077 | N | 1.1313 | 7.5706 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 23.93 | 0.17 | N2 | 27.0876 | 0.2469 | N1 | 23.9273 | 0.16862 | N | 41.3195 | 239.783 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.12 | 2.07 | N2 | 1.3371 | 0.96558 | N1 | 1.1237 | 2.0667 | N | 1.3021 | 10.8386 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 47.09 | 41.51 | N2 | 53.5075 | 0.97789 | N1 | 47.0924 | 41.5083 | N | 47.2839 | 51.8921 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.1 | 1.16 | N2 | 1.2842 | 1.5363 | N1 | 1.1029 | 1.1553 | N | 1.2102 | 9.2424 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 3.41 | 0.6 | N2 | 3.4348 | 2.3284 | N1 | 3.4149 | 0.59504 | N | 4.5483 | 38.8968 | 0 | 0.1 | 0 | 0 | 0 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 3.7 | 4.54 | N2 | 3.9189 | 1.2235 | N1 | 3.6995 | 4.5418 | N | 3.8155 | 10.7388 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 3.39 | 1.24 | N2 | 3.6192 | 0.82289 | N1 | 3.3873 | 1.2358 | N | 3.4722 | 8.2048 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 4.56 | 5.27 | N2 | 4.6464 | 1.0716 | N1 | 4.5553 | 5.2661 | N | 4.8172 | 16.888 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 3.49 | 1.22 | N2 | 3.499 | 1.2209 | N1 | 3.4942 | 1.2232 | N | 3.995 | 17.8104 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 7.38 | 1.92 | N2 | 7.4222 | 1.9199 | N1 | 7.3795 | 1.9206 | N | 12.4643 | 165.8629 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 6.44 | 5.36 | N2 | 6.483 | 2.1518 | N1 | 6.4422 | 5.3622 | N | 7.0598 | 33.1945 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 3.74 | 0.69 | N2 | 3.7385 | 0.69113 | N1 | 3.8489 | 0.54092 | N | 5.4273 | 58.7465 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 3.21 | 0.42 | N2 | 3.7385 | 0.69113 | N1 | 3.2103 | 0.42454 | N | 4.5519 | 47.5842 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.27 | 2.01 | N2 | 1.286 | 1.08 | N1 | 1.269 | 2.0125 | N | 1.6784 | 16.9752 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 1.51 | 0.46 | N2 | 1.5122 | 0.45908 | N1 | 1.5072 | 0.45925 | N | 2.6063 | 39.4257 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 9.43 | 9.01 | N2 | 9.8856 | 0.69672 | N1 | 9.4308 | 9.0081 | N | 10.7871 | 57.5509 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 0.96 | 0.94 | N2 | 1.0146 | 0.41835 | N1 | 0.96255 | 0.94053 | N | 0.98762 | 3.4953 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 2.92 | 0.56 | N2 | 2.9371 | 0.5602 | N1 | 2.9161 | 0.5604 | N | 4.3252 | 48.3976 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 0.95 | 1.24 | N2 | 1.1342 | 1.0868 | N1 | 0.94737 | 1.2392 | N | 1.0684 | 7.957 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 4.19 | 4.45 | N2 | 4.3762 | 0.30264 | N1 | 4.1898 | 4.4461 | N | 4.8203 | 26.1349 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 1.99 | 1.56 | N2 | 2.3085 | 0.28272 | N1 | 1.9929 | 1.5621 | N | 2.3901 | 24.2991 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-2 | 7.29 | 0.96 | N2 | 7.2919 | 0.95986 | N1 | 7.315 | 3.0801 | N | 9.3757 | 84.7952 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 7.55 | 7.06 | N2 | 7.6483 | 0.99269 | N1 | 7.5512 | 7.0567 | N | 9.7716 | 85.7293 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.43 | 0.9 | N2 | 0.55812 | 0.07737 | N1 | 0.44365 | 0.74511 | N | 0.43262 | 0.89834 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 0.74 | 1.13 | N2 | 0.86673 | 0.53303 | N1 | 0.73556 | 1.1295 | N | 0.73609 | 4.8123 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 3.49 | 3.9 | N2 | 3.5303 | 0.73683 | N1 | 3.4895 | 3.8977 | N | 5.2587 | 63.6576 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 11.38 | 3.17 | N2 | 11.4391 | 3.1672 | N1 | 11.3764 | 3.1683 | N | 21.0457 | 273.5854 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.07 | 1.77 | N2 | 1.1117 | 0.9424 | N1 | 1.0703 | 1.7671 | N | 1.2174 | 7.7267 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 4.42 | 0.84 | N2 | 4.5779 | 0.58627 | N1 | 4.415 | 0.84345 | N | 5.7858 | 49.82 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 22.67 | 2.39 | N2 | 23.42 | 0.70853 | N1 | 22.6695 | 2.3921 | N | 24.1836 | 65.4055 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 8.69 | 5.49 | N2 | 8.7007 | 5.4883 | N1 | 8.6926 | 5.4891 | N | 25.6206 | 526.2835 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 5.41 | 0.81 | N2 | 5.5766 | 0.33132 | N1 | 5.4137 | 0.81341 | N | 6.0394 | 28.3258 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 4.76 | 1.52 | N2 | 4.7932 | 1.5186 | N1 | 4.7635 | 1.5192 | N | 8.7438 | 131.2074 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 3.16 | 2.17 | N2 | 3.1626 | 2.1637 | N1 | 3.1574 | 2.1652 | N | 3.8579 | 168.1609 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 3.05 | 6.08 | N2 | 3.1954 | 1.0779 | N1 | 3.0457 | 6.0838 | N | 3.1172 | 9.073 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 5.02 | 4.52 | N2 | 5.1058 | 0.39753 | N1 | 5.0207 | 4.516 | N | 5.6952 | 30.3129 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 4.44 | 0.85 | N2 | 5.0643 | 1.2223 | N1 | 4.4445 | 0.85001 | N | 6.3432 | 85.2723 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.15 | 2.03 | N2 | 1.1781 | 1.5015 | N1 | 1.1501 | 2.0276 | N | 1.4049 | 11.9164 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 12.21 | 14 | N2 | 12.4681 | 0.88536 | N1 | 12.2052 | 13.9977 | N | 13.1939 | 58.35 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 20.11 | 0.81 | N2 | 20.1078 | 0.81102 | N1 | 20.1076 | 0.81115 | N | 31.7516 | 152.0924 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.22 | 1.86 | N2 | 1.4314 | 0.5145 | N1 | 1.2179 | 1.8576 | N | 1.3165 | 7.4614 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 3.23 | 2.98 | N2 | 3.4075 | 0.4117 | N1 | 3.2308 | 2.9842 | N | 3.2308 | 2.9842 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 8.44 | 2.17 | N2 | 8.4432 | 2.1723 | N1 | 8.4421 | 2.1726 | N | 14.9861 | 200.5269 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 12.1 | 0.77 | N2 | 12.0984 | 0.76687 | N1 | 12.0981 | 0.767 | N | 15.21 | 40.4329 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 14.07 | 0.78 | N2 | 14.1034 | 0.77552 | N1 | 14.0733 | 0.77567 | N | 16.8369 | 35.9873 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 18.51 | 0.81 | N2 | 18.5086 | 0.81407 | N1 | 18.5079 | 0.81424 | N | 19.8735 | 55.7265 | 0 | 0 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 6.8 | 1.89 | N2 | 6.8408 | 1.8856 | N1 | 6.8011 | 1.8863 | N | 11.8779 | 162.9016 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 2.89 | 4.42 | N2 | 3.0778 | 0.84477 | N1 | 2.8926 | 4.4154 | N | 2.9625 | 7.277 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 4.59 | 0.67 | N2 | 4.765 | 0.46927 | N1 | 4.5932 | 0.66544 | N | 5.553 | 39.9263 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.01 | 2.08 | N2 | 1.0266 | 1.3254 | N1 | 1.0105 | 2.0817 | N | 1.2375 | 10.8687 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 13.97 | 22.81 | N2 | 13.9741 | 22.8037 | N1 | 13.9672 | 22.8124 | N | 93.7912 | 2070.0853 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 34.8 | 110.59 | N2 | 34.8994 | 110.5522 | N1 | 34.7998 | 110.593 | N | 90.678 | 9658.7327 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 9.82 | 10.8 | N2 | 9.8941 | 1.7731 | N1 | 9.8205 | 10.7952 | N | 14.1559 | 153.1429 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 3.3 | 0.93 | N2 | 3.322 | 0.93191 | N1 | 3.2993 | 0.93225 | N | 5.5983 | 80.5173 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 7.91 | 1.64 | N2 | 8.3369 | 1.1884 | N1 | 7.9068 | 1.6369 | N | 8.0872 | 20.3326 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 18.19 | 2.77 | N2 | 18.202 | 2.7649 | N1 | 18.1863 | 2.7664 | N | 18.7007 | 68.5889 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 6.47 | 8.87 | N2 | 6.6519 | 1.946 | N1 | 6.4712 | 8.8731 | N | 6.6409 | 16.1213 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 4.25 | 2.12 | N2 | 4.256 | 2.123 | N1 | 4.25 | 2.1238 | N | 10.0059 | 182.3188 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 2.61 | 3.17 | N2 | 2.779 | 0.88036 | N1 | 2.6131 | 3.1673 | N | 2.6847 | 7.7067 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 6.69 | 8.53 | N2 | 7.2135 | 1.0202 | N1 | 6.6878 | 8.5331 | N | 6.6877 | 8.5331 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 0.9 | 0.65 | N2 | 0.99758 | 0.07112 | N1 | 0.9027 | 0.64612 | N | 0.90262 | 0.64612 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 10.58 | 1.73 | N2 | 10.637 | 1.7327 | N1 | 10.578 | 1.7333 | N | 15.2893 | 149.6567 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 9.3 | 4.13 | N2 | 9.3497 | 4.1291 | N1 | 9.2977 | 4.1296 | N | 21.7782 | 392.4585 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.09 | 3.49 | N2 | 1.393 | 0.23525 | N1 | 1.1207 | 3.4759 | N | 1.09 | 3.4935 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 11.77 | 5.49 | N2 | 12.2574 | 1.7115 | N1 | 11.7704 | 5.4861 | N | 16.8338 | 161.3751 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 4.26 | 1.56 | N2 | 4.5065 | 1.4001 | N1 | 4.2632 | 1.5647 | N | 4.4197 | 12.7028 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 1.72 | 1.78 | N2 | 1.7203 | 1.7837 | N1 | 1.7152 | 1.7845 | N | 1.9374 | 14.1558 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 2.31 | 0.85 | N2 | 2.4867 | 0.52435 | N1 | 2.3074 | 0.847 | N | 2.3396 | 4.591 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25length130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 195 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 195 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 195 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 390 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 20 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 195 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 195 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 195 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 195 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 195 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 390 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 390 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 195 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 195 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 195 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 195 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 195 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 195 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 195 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 195 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 195 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 195 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 195 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 195 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 195 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 195 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 195 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 195 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 195 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 195 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 195 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 195 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 20 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 195 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 39 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 195 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 39 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 195 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 195 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 195 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 195 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 195 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 39 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 39 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 39 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 195 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 195 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 195 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 195 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 195 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 195 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 195 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 195 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 195 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 195 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 195 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 195 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 195 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 195 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 195 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 195 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 195 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 195 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 195 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 195 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 195 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 195 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 195 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 195 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 195 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 195 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 20 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 195 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 195 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 39 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 20 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 20 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 39 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 195 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 195 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 195 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 195 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 195 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 195 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 195 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 195 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 195 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 195 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 195 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 195 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 195 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 195 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 195 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 195 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 195 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 195 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 195 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 195 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 195 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 195 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 13.46 | 15.87 | N2 | 13.5554 | 0.97941 | N1 | 13.4623 | 15.8685 | N | 14.7529 | 65.1498 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 12.65 | 8.67 | N2 | 12.6759 | 8.6623 | N1 | 12.6546 | 8.6665 | N | 16.3938 | 798.4268 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 6.07 | 1.22 | N2 | 6.4138 | 0.53875 | N1 | 6.0668 | 1.2176 | N | 7.3446 | 50.0643 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 3.42 | 14.69 | N2 | 4.3258 | 1.3491 | N1 | 3.4828 | 3.6349 | N | 3.4234 | 14.6914 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 36.43 | 0.32 | N2 | 41.6244 | 0.64193 | N1 | 36.4325 | 0.31632 | N | 67.5397 | 421.1201 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 9.32 | 2.71 | N2 | 9.3811 | 2.7061 | N1 | 9.3161 | 2.7068 | N | 16.8326 | 254.7207 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 4.35 | 4.46 | N2 | 4.4302 | 1.0162 | N1 | 4.3475 | 4.463 | N | 6.5438 | 80.0558 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 2.28 | 9.76 | N2 | 2.4134 | 3.7437 | N1 | 2.2789 | 9.7579 | N | 2.2908 | 30.0452 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 3.41 | 18.3 | N2 | 3.593 | 7.0195 | N1 | 3.4114 | 18.2961 | N | 3.4797 | 56.3347 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.84 | 1.15 | N2 | 2.8676 | 1.1493 | N1 | 2.8357 | 1.15 | N | 6.025 | 91.0451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 15.96 | 5.15 | N2 | 19.0023 | 1.6359 | N1 | 15.9602 | 5.1514 | N | 18.8727 | 166.949 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 11.28 | 1.55 | N2 | 13.183 | 3.1544 | N1 | 11.2835 | 1.5488 | N | 14.0983 | 148.6851 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 39.3 | 6.16 | N2 | 39.765 | 5.206 | N1 | 39.3027 | 6.1581 | N | 54.1362 | 455.8494 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 4.23 | 1.83 | N2 | 5.0033 | 0.91655 | N1 | 4.2272 | 1.8345 | N | 5.5724 | 61.2339 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 10.08 | 0.75 | N2 | 10.4879 | 0.2763 | N1 | 10.0755 | 0.74931 | N | 10.4095 | 22.7301 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.65 | 2.77 | N2 | 2.78 | 1.3595 | N1 | 2.647 | 2.7734 | N | 2.8233 | 10.7054 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 3.64 | 2.08 | N2 | 3.6852 | 0.39236 | N1 | 3.6423 | 2.0821 | N | 4.2009 | 26.1012 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 4.04 | 2.42 | N2 | 4.315 | 0.34366 | N1 | 4.0374 | 2.4156 | N | 4.0374 | 2.4156 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 6.24 | 4.88 | N2 | 6.4167 | 1.559 | N1 | 6.2435 | 4.8831 | N | 9.8023 | 122.8026 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 5.84 | 5.22 | N2 | 6.37 | 0.92601 | N1 | 5.844 | 5.2221 | N | 5.8755 | 7.7501 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 41.25 | 24.21 | N2 | 41.2955 | 24.1964 | N1 | 41.2493 | 24.2081 | N | 125.6291 | 2233.3657 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 3.5 | 0.76 | N2 | 4.0622 | 1.5628 | N1 | 3.504 | 0.75886 | N | 5.6111 | 75.6698 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 7.19 | 9.03 | N2 | 7.2748 | 1.6052 | N1 | 7.1908 | 9.0306 | N | 11.6952 | 151.0915 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.83 | 1.08 | N2 | 1.0006 | 1.3074 | N1 | 0.833 | 1.083 | N | 0.85274 | 5.5005 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 4.07 | 3.91 | N2 | 4.1524 | 0.82699 | N1 | 4.0745 | 3.9066 | N | 5.9028 | 65.1452 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.97 | 2.05 | N2 | 4.0282 | 0.51667 | N1 | 3.9746 | 2.052 | N | 4.9332 | 40.9152 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 5.62 | 6.17 | N2 | 5.7145 | 1.2626 | N1 | 5.6154 | 6.1681 | N | 8.4299 | 100.0043 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 8.48 | 8.8 | N2 | 8.6627 | 3.9882 | N1 | 8.4774 | 8.7992 | N | 9.5077 | 315.9321 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.66 | 2.68 | N2 | 2.796 | 1.613 | N1 | 2.6568 | 2.6788 | N | 2.8765 | 13.3061 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 10.26 | 8.72 | N2 | 10.4491 | 1.7243 | N1 | 10.2614 | 8.7227 | N | 14.1832 | 136.322 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 4.93 | 5.01 | N2 | 5.0198 | 0.9284 | N1 | 4.9297 | 5.0072 | N | 7.0223 | 73.529 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.93 | 2.8 | N2 | 2.3573 | 0.32501 | N1 | 1.9301 | 2.8 | N | 2.0938 | 14.0596 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 41.65 | 0.26 | N2 | 47.5694 | 0.37598 | N1 | 41.6501 | 0.26361 | N | 72.7403 | 431.2744 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 2.06 | 0.58 | N2 | 2.4412 | 0.35843 | N1 | 2.0578 | 0.585 | N | 2.4112 | 20.1288 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 85.62 | 73.17 | N2 | 97.8945 | 1.1923 | N1 | 85.6218 | 73.1686 | N | 85.8133 | 83.5524 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 2.03 | 1.07 | N2 | 2.3565 | 0.28798 | N1 | 2.0313 | 1.0728 | N | 2.2404 | 17.1644 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 5.33 | 5.71 | N2 | 5.4049 | 0.78161 | N1 | 5.3321 | 5.7078 | N | 7.3068 | 65.0572 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 6.61 | 10.81 | N2 | 7.0434 | 1.1835 | N1 | 6.6061 | 10.81 | N | 6.8025 | 18.2559 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 6.09 | 1.9 | N2 | 6.5391 | 1.4042 | N1 | 6.094 | 1.8961 | N | 6.1911 | 12.8797 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 8.11 | 6.98 | N2 | 8.2791 | 0.46438 | N1 | 8.1093 | 6.9772 | N | 8.6199 | 30.7806 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 6.43 | 0.38 | N2 | 6.4433 | 0.38434 | N1 | 6.4266 | 0.38478 | N | 7.4289 | 33.4868 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 13.13 | 3.2 | N2 | 13.2183 | 3.1995 | N1 | 13.1326 | 3.2003 | N | 22.4026 | 301.1651 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 10.08 | 7.26 | N2 | 10.1309 | 1.2608 | N1 | 10.0849 | 7.2639 | N | 11.2179 | 58.939 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 5.89 | 1.24 | N2 | 5.8884 | 1.243 | N1 | 6.1106 | 7.7675 | N | 8.8699 | 100.3548 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 5.06 | 0.76 | N2 | 5.8884 | 1.243 | N1 | 5.0554 | 0.75795 | N | 7.2351 | 79.5914 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 2.3 | 2.2 | N2 | 2.3447 | 0.4009 | N1 | 2.3012 | 2.2046 | N | 3.1123 | 31.5827 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.74 | 0.93 | N2 | 2.7525 | 0.93098 | N1 | 2.7357 | 0.93157 | N | 4.8378 | 73.3499 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 16.74 | 9.53 | N2 | 17.8162 | 0.46584 | N1 | 16.744 | 9.5284 | N | 19.3828 | 100.7519 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.72 | 1.51 | N2 | 1.8262 | 0.7696 | N1 | 1.7206 | 1.5136 | N | 1.7768 | 6.2787 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 5.16 | 1.11 | N2 | 5.2026 | 1.1095 | N1 | 5.159 | 1.1102 | N | 7.7694 | 87.8755 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.74 | 1.41 | N2 | 2.1002 | 1.0366 | N1 | 1.7423 | 1.4103 | N | 1.9771 | 14.7773 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 7.42 | 7.27 | N2 | 7.8094 | 0.58145 | N1 | 7.4195 | 7.2713 | N | 8.5907 | 45.646 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 3.63 | 2.9 | N2 | 4.2301 | 0.57347 | N1 | 3.6254 | 2.901 | N | 4.4309 | 45.1269 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 12.89 | 17.2 | N2 | 12.9886 | 1.9017 | N1 | 12.8901 | 17.2023 | N | 16.7799 | 152.4416 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 13.4 | 12.89 | N2 | 13.6254 | 1.9669 | N1 | 13.3965 | 12.8904 | N | 17.5051 | 155.6905 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.76 | 1.65 | N2 | 1.001 | 0.13401 | N1 | 0.77626 | 1.3662 | N | 0.76314 | 1.6461 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.35 | 2.1 | N2 | 1.6106 | 0.99876 | N1 | 1.3525 | 2.0977 | N | 1.3602 | 8.9372 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 6.17 | 7.11 | N2 | 6.2641 | 1.4593 | N1 | 6.1662 | 7.1127 | N | 9.4464 | 115.5834 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 20.27 | 5.28 | N2 | 20.3909 | 5.2778 | N1 | 20.265 | 5.2791 | N | 37.8401 | 496.7879 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.9 | 3.23 | N2 | 1.9931 | 1.7486 | N1 | 1.9036 | 3.2329 | N | 2.1776 | 14.0299 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 7.85 | 1.17 | N2 | 8.1716 | 0.97962 | N1 | 7.8537 | 1.1749 | N | 10.3494 | 88.8118 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 40.63 | 3.05 | N2 | 42.1388 | 1.2886 | N1 | 40.627 | 3.0478 | N | 43.5475 | 119.7652 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 15.4 | 10.01 | N2 | 15.4235 | 10.0071 | N1 | 15.396 | 10.0096 | N | 45.8927 | 946.6367 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 9.66 | 0.96 | N2 | 9.9791 | 0.61105 | N1 | 9.6604 | 0.9622 | N | 10.843 | 50.7633 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 8.46 | 2.53 | N2 | 8.5201 | 2.5309 | N1 | 8.4596 | 2.5315 | N | 15.735 | 238.2274 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 5.8 | 4.69 | N2 | 5.8186 | 4.6858 | N1 | 5.801 | 4.6908 | N | 7.1642 | 313.4152 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 5.44 | 10.51 | N2 | 5.7472 | 1.9212 | N1 | 5.4382 | 10.5107 | N | 5.573 | 15.8885 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 8.91 | 8.29 | N2 | 9.0827 | 0.83141 | N1 | 8.9085 | 8.2914 | N | 10.2028 | 55.2062 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 7.82 | 1.56 | N2 | 9.0065 | 2.0369 | N1 | 7.8164 | 1.5622 | N | 11.2906 | 153.6438 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 2.11 | 2.46 | N2 | 2.1726 | 0.28146 | N1 | 2.1089 | 2.4624 | N | 2.6037 | 22.1714 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 21.67 | 25.53 | N2 | 22.2433 | 2.0627 | N1 | 21.6651 | 25.531 | N | 23.5411 | 106.0347 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 35.32 | 0.24 | N2 | 35.3186 | 0.23606 | N1 | 35.3184 | 0.23608 | N | 56.2164 | 273.8197 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 2.25 | 2.71 | N2 | 2.6598 | 0.93567 | N1 | 2.2456 | 2.7065 | N | 2.4377 | 13.8569 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 5.99 | 5.59 | N2 | 6.3316 | 0.73345 | N1 | 5.9942 | 5.5887 | N | 5.9942 | 5.5887 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 13.07 | 4.28 | N2 | 13.069 | 4.2837 | N1 | 13.0654 | 4.2849 | N | 24.923 | 359.7169 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 17.71 | 0.99 | N2 | 17.7067 | 0.98788 | N1 | 17.7059 | 0.98806 | N | 22.4881 | 62.3175 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 20.43 | 0.97 | N2 | 20.4722 | 0.97344 | N1 | 20.4314 | 0.97366 | N | 24.702 | 55.7943 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 29.96 | 7.91 | N2 | 30.129 | 1.4547 | N1 | 29.9562 | 7.9082 | N | 32.5041 | 97.3454 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 12.1 | 3.14 | N2 | 12.1791 | 3.1424 | N1 | 12.0991 | 3.1432 | N | 21.3579 | 295.7857 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 5.16 | 7.43 | N2 | 5.5355 | 1.4998 | N1 | 5.1605 | 7.4337 | N | 5.2915 | 12.5564 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 8.18 | 0.93 | N2 | 8.5084 | 0.77808 | N1 | 8.1755 | 0.92535 | N | 9.9128 | 70.5232 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.79 | 2.71 | N2 | 1.8328 | 1.2535 | N1 | 1.7908 | 2.706 | N | 2.2167 | 19.7339 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 25.05 | 42.49 | N2 | 25.0703 | 42.4606 | N1 | 25.047 | 42.4903 | N | 171.367 | 3793.629 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 62.14 | 201.19 | N2 | 62.3406 | 201.0573 | N1 | 62.14 | 201.1949 | N | 163.9138 | 17594.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 17.43 | 19.72 | N2 | 17.6374 | 2.9545 | N1 | 17.4322 | 19.7152 | N | 25.3857 | 278.0987 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 5.83 | 4.48 | N2 | 5.8919 | 1.5531 | N1 | 5.8317 | 4.4782 | N | 10.0694 | 146.1902 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 14.16 | 1.01 | N2 | 14.9812 | 0.38727 | N1 | 14.1552 | 1.0139 | N | 14.4733 | 34.9851 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 32.3 | 2.44 | N2 | 32.3509 | 2.439 | N1 | 32.2969 | 2.441 | N | 33.234 | 124.9005 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 11.58 | 14.96 | N2 | 11.9101 | 0.40031 | N1 | 11.5827 | 14.9577 | N | 11.8988 | 29.0067 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 7.82 | 3.61 | N2 | 7.8422 | 3.607 | N1 | 7.8218 | 3.6079 | N | 18.5951 | 339.1985 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 4.67 | 5.02 | N2 | 4.9992 | 1.6465 | N1 | 4.6745 | 5.015 | N | 4.819 | 13.4826 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 12.01 | 15.24 | N2 | 13.0058 | 1.8978 | N1 | 12.0133 | 15.2405 | N | 12.0132 | 15.2405 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.62 | 1.05 | N2 | 1.8005 | 0.13278 | N1 | 1.6168 | 1.0496 | N | 1.6167 | 1.0496 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 18.85 | 2.89 | N2 | 18.9644 | 2.8872 | N1 | 18.8463 | 2.8879 | N | 27.4162 | 271.7689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 16.55 | 7.57 | N2 | 16.6537 | 7.5702 | N1 | 16.5497 | 7.572 | N | 39.2469 | 712.5635 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 2.02 | 6.49 | N2 | 2.5886 | 0.3751 | N1 | 2.0674 | 6.4552 | N | 2.0171 | 6.488 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 20.96 | 6.9 | N2 | 22.0229 | 3.0835 | N1 | 20.9604 | 6.901 | N | 30.0572 | 285.3449 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 7.61 | 10.79 | N2 | 8.1153 | 1.3193 | N1 | 7.6085 | 10.7944 | N | 7.8671 | 20.6681 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 3.15 | 0.33 | N2 | 3.1683 | 0.33436 | N1 | 3.1511 | 0.33457 | N | 3.5927 | 26.3379 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 4.16 | 1.31 | N2 | 4.4893 | 0.11794 | N1 | 4.1586 | 1.3073 | N | 4.209 | 7.8487 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25MD70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 78.1 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 70 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 18 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 2.5 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 253.1 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 47 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 15.5 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 5.6 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 10.5 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 7 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 26.6 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 15.4 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 304.5 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 18.9 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 33.4 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 7.5 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 9.1 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 12.1 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 28 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 21.1 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 399.7 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 12.3 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 31.5 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 1.4 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 14 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 12.4 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 21.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 42 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 5.6 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 56 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 17.5 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 5.9 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 312.2 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 5.9 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 219.2 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 5.6 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 99.3 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 24.5 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 16.6 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 33.3 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 17.4 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 80.8 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 261 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 113.4 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 113.4 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 5.5 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 7.1 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 72.8 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 2.9 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 18.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 4.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 28.8 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 14.5 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 79.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 85.4 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.4 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 3.1 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 24.9 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 159.1 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 4 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 30.8 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 297.3 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 100.5 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 34 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 40.3 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 20.4 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 17.8 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 38.4 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 44.3 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 4.9 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 185 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 196 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 7 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 23.8 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 373 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 584.5 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 722.8 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 775.2 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 71 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 16.8 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 32.9 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 3.4 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 146.8 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 675.7 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 127.7 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 22.5 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 69.2 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 331.7 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 50.7 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 37.9 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 14.3 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 55.6 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 2.4 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 143 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 114.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 6.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 126 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 26.3 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 9.1 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 8.4 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 78.08 | 36118.62 | 0 | 3 | N-1 | 8.23 | 8.5 | N2 | 8.3257 | 0.48893 | N1 | 8.2332 | 8.4998 | N | 8.86 | 34.9776 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 70 | 6050 | 0 | 3 | N-1 | 7.78 | 5.98 | N2 | 7.7894 | 5.9703 | N1 | 7.7777 | 5.9756 | N | 9.6812 | 429.1472 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18.03 | 34827.32 | 2 | 4 | N-1 | 3.79 | 0.88 | N2 | 4.0009 | 0.29205 | N1 | 3.7869 | 0.88399 | N | 4.426 | 27.361 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 2.5 | 33792.6 | 1 | 1 | N-0 | 2.09 | 7.95 | N2 | 2.6776 | 0.72122 | N1 | 2.1471 | 7.9453 | N | 2.0898 | 7.9453 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 253.13 | 90000 | 3 | 1 | N-1 | 22.81 | 3.95 | N2 | 26.0019 | 0.37569 | N1 | 22.8077 | 3.9466 | N | 39.5556 | 232.5709 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 47.02 | 34024.46 | 2 | 2 | N-1 | 5.78 | 7.47 | N2 | 5.8443 | 1.6725 | N1 | 5.78 | 7.4692 | N | 9.7762 | 138.2175 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 15.52 | 33835.17 | 0 | 2 | N-1 | 2.69 | 2.4 | N2 | 2.7419 | 0.52414 | N1 | 2.6869 | 2.398 | N | 3.8119 | 43.0677 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 5.6 | 6050 | 2 | 2 | N-0 | 1.41 | 16.3 | N2 | 1.5019 | 2.0985 | N1 | 1.4144 | 16.3032 | N | 1.4143 | 16.3032 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 10.5 | 6050 | 2 | 2 | N-1 | 2.12 | 9.91 | N2 | 2.2316 | 3.9346 | N1 | 2.1179 | 9.9119 | N | 2.1395 | 30.5684 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 7 | 39506.97 | 2 | 2 | N-1 | 1.79 | 0.6 | N2 | 1.8082 | 0.59774 | N1 | 1.7878 | 0.59804 | N | 3.4654 | 49.4043 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 26.6 | 34429.94 | 2 | 1 | N-1 | 9.88 | 8.29 | N2 | 11.758 | 1.1282 | N1 | 9.8849 | 8.2922 | N | 11.2229 | 90.2492 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 15.4 | 34429.94 | 0 | 1 | N-1 | 6.96 | 0.83 | N2 | 8.1188 | 1.68 | N1 | 6.9615 | 0.83397 | N | 8.2667 | 80.0612 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 304.5 | 37279.21 | 4 | 5 | N-1 | 24.39 | 3.46 | N2 | 24.6616 | 2.8396 | N1 | 24.3853 | 3.4564 | N | 32.255 | 247.4514 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 18.89 | 35252.82 | 0 | 1 | N-1 | 2.62 | 2.41 | N2 | 3.0927 | 0.47271 | N1 | 2.6173 | 2.4071 | N | 3.2578 | 32.9721 | 0 | 0 | 0 | 0 | 0.3 | 0
| 15 | 33.42 | 36373.37 | 3 | 6 | N-1 | 6.24 | 1.73 | N2 | 6.5002 | 1.4882 | N1 | 6.2443 | 1.7319 | N | 6.3924 | 12.5334 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 7.47 | 38166.21 | 0 | 2 | N-1 | 1.62 | 2.35 | N2 | 1.7047 | 0.72863 | N1 | 1.6192 | 2.3462 | N | 1.7053 | 5.7585 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 9.1 | 34357.34 | 3 | 3 | N-1 | 2.27 | 2.59 | N2 | 2.3007 | 1.7735 | N1 | 2.2715 | 2.5883 | N | 2.5431 | 14.147 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 12.08 | 34357.34 | 3 | 3 | N-0 | 2.51 | 1.31 | N2 | 2.6824 | 0.17946 | N1 | 2.5055 | 1.3085 | N | 2.5054 | 1.3085 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 28 | 34357.34 | 0 | 2 | N-1 | 3.85 | 2.62 | N2 | 3.9554 | 0.80404 | N1 | 3.8458 | 2.6217 | N | 5.6941 | 66.0635 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 21.11 | 33830.95 | 2 | 3 | N-1 | 3.62 | 2.92 | N2 | 3.9484 | 0.53553 | N1 | 3.6194 | 2.917 | N | 3.6302 | 4.314 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 399.72 | 39574.74 | 4 | 3 | N-1 | 25.57 | 12.95 | N2 | 25.5889 | 12.9452 | N1 | 25.5669 | 12.9501 | N | 70.8738 | 1206.1531 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 12.29 | 37690.78 | 2 | 1 | N-1 | 2.21 | 0.41 | N2 | 2.5481 | 0.96575 | N1 | 2.2117 | 0.41098 | N | 3.2855 | 41.4277 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 31.54 | 35546.67 | 2 | 2 | N-1 | 4.47 | 4.89 | N2 | 4.5392 | 0.99209 | N1 | 4.4722 | 4.8895 | N | 6.8452 | 81.9851 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.37 | 34513.16 | 0 | 1 | N-0 | 0.52 | 2.96 | N2 | 0.61629 | 0.70099 | N1 | 0.51669 | 0.50612 | N | 0.51535 | 2.9618 | 0 | 0 | 0 | 0 | 0 | 0
| 25 | 14 | 35460.24 | 0 | 2 | N-1 | 2.52 | 2.1 | N2 | 2.5724 | 0.42653 | N1 | 2.5207 | 2.099 | N | 3.4491 | 35.0459 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 12.37 | 35460.24 | 2 | 2 | N-1 | 2.49 | 3.57 | N2 | 2.5302 | 1.3935 | N1 | 2.4919 | 3.5719 | N | 2.9549 | 22.2007 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 21.54 | 34721.47 | 2 | 2 | N-1 | 3.5 | 3.34 | N2 | 3.5734 | 0.65665 | N1 | 3.5032 | 3.3397 | N | 4.967 | 54.2641 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 42 | 6050 | 2 | 2 | N-1 | 5.29 | 4.76 | N2 | 5.403 | 2.0743 | N1 | 5.2915 | 4.7559 | N | 5.7572 | 171.4349 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 5.6 | 34432.4 | 2 | 3 | N-1 | 1.65 | 2.45 | N2 | 1.7341 | 0.87163 | N1 | 1.6464 | 2.4528 | N | 1.7555 | 7.2691 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 56.02 | 36683.18 | 3 | 2 | N-1 | 6.39 | 4.7 | N2 | 6.517 | 0.89081 | N1 | 6.387 | 4.7006 | N | 8.4112 | 73.5293 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 17.54 | 36353.07 | 2 | 2 | N-1 | 3.08 | 2.71 | N2 | 3.1437 | 0.48282 | N1 | 3.0803 | 2.7115 | N | 4.1559 | 39.8979 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 5.88 | 32848.83 | 0 | 1 | N-1 | 1.18 | 1.51 | N2 | 1.4492 | 0.17163 | N1 | 1.1847 | 1.5077 | N | 1.2547 | 7.5706 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 312.21 | 90000 | 3 | 1 | N-1 | 26.1 | 4.78 | N2 | 29.7121 | 0.21627 | N1 | 26.1022 | 4.7839 | N | 42.4573 | 234.8701 | 0 | 0 | 0 | 0 | 0.1 | 0
| 34 | 5.93 | 38350 | 0 | 1 | N-1 | 1.27 | 2.07 | N2 | 1.5186 | 0.97377 | N1 | 1.2682 | 2.0667 | N | 1.4261 | 10.8386 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 219.19 | 40649.71 | 2 | 4 | N-1 | 52.56 | 40.1 | N2 | 60.2465 | 0.75795 | N1 | 52.563 | 40.0961 | N | 52.6801 | 47.3648 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 5.6 | 38350 | 0 | 1 | N-1 | 1.25 | 1.16 | N2 | 1.4597 | 1.543 | N1 | 1.2511 | 1.1553 | N | 1.3299 | 9.2424 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 99.32 | 39149.41 | 2 | 2 | N-1 | 3.48 | 3.18 | N2 | 3.5355 | 0.42173 | N1 | 3.4787 | 3.1837 | N | 4.5122 | 36.3821 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 24.53 | 34247.59 | 2 | 3 | N-1 | 4.08 | 6.06 | N2 | 4.3646 | 1.2146 | N1 | 4.0805 | 6.0605 | N | 4.1809 | 10.1395 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 16.63 | 34693 | 2 | 5 | N-1 | 3.77 | 1.09 | N2 | 4.0458 | 0.77236 | N1 | 3.7723 | 1.0909 | N | 3.8147 | 7.3692 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 33.26 | 35142.51 | 3 | 3 | N-1 | 5.03 | 5.22 | N2 | 5.1562 | 1.0829 | N1 | 5.0293 | 5.2222 | N | 5.2697 | 16.6701 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 17.36 | 40211.29 | 0 | 6 | N-1 | 3.97 | 1.28 | N2 | 3.977 | 1.274 | N1 | 3.9673 | 1.2772 | N | 4.4518 | 17.9209 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 80.85 | 36003.25 | 2 | 2 | N-1 | 8.17 | 1.98 | N2 | 8.2214 | 1.9776 | N1 | 8.1693 | 1.9786 | N | 13.0625 | 163.4157 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 260.97 | 36329.98 | 3 | 2 | N-1 | 6.56 | 5.33 | N2 | 6.6161 | 2.2077 | N1 | 6.5615 | 5.3316 | N | 7.09 | 32.2447 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 113.4 | 37364.49 | 1 | 2 | N-2 | 3.85 | 0.67 | N2 | 3.8466 | 0.67071 | N1 | 3.9745 | 2.5547 | N | 5.3787 | 55.6828 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 113.4 | 37364.49 | 1 | 1 | N-1 | 3.31 | 0.41 | N2 | 3.8466 | 0.67071 | N1 | 3.3076 | 0.41387 | N | 4.4341 | 44.5115 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 5.54 | 35222.85 | 0 | 2 | N-1 | 1.43 | 2.01 | N2 | 1.4604 | 1.0892 | N1 | 1.4309 | 2.0147 | N | 1.83 | 16.9906 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 7.14 | 33960.97 | 0 | 2 | N-1 | 1.71 | 0.48 | N2 | 1.7155 | 0.48019 | N1 | 1.7057 | 0.48043 | N | 2.784 | 39.4609 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 72.85 | 36864.7 | 1 | 6 | N-1 | 10.39 | 6.48 | N2 | 11.0427 | 0.66606 | N1 | 10.3925 | 6.4831 | N | 11.7167 | 55.3147 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 2.86 | 32176.46 | 1 | 3 | N-1 | 1.07 | 1.52 | N2 | 1.1361 | 0.41534 | N1 | 1.0687 | 1.5171 | N | 1.0905 | 3.4188 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 18.54 | 37146.71 | 2 | 2 | N-1 | 3.23 | 0.58 | N2 | 3.2563 | 0.57701 | N1 | 3.229 | 0.57729 | N | 4.5735 | 47.6829 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 4.66 | 38350 | 0 | 1 | N-1 | 1.07 | 1.24 | N2 | 1.2915 | 1.0916 | N1 | 1.0722 | 1.2392 | N | 1.1756 | 7.957 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 28.76 | 38401.47 | 2 | 3 | N-1 | 4.62 | 4.1 | N2 | 4.8679 | 0.30529 | N1 | 4.6166 | 4.0957 | N | 5.207 | 25.1071 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 14.48 | 34311.06 | 0 | 1 | N-1 | 2.25 | 1.56 | N2 | 2.6208 | 0.29575 | N1 | 2.2481 | 1.5621 | N | 2.6045 | 24.2991 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 79.2 | 35530.24 | 1 | 2 | N-1 | 8 | 10.14 | N2 | 8.0799 | 0.98885 | N1 | 7.9991 | 10.1373 | N | 9.9926 | 83.0092 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 85.4 | 35530.24 | 2 | 2 | N-1 | 8.31 | 6.98 | N2 | 8.4743 | 1.0227 | N1 | 8.3114 | 6.9754 | N | 10.4369 | 84.4719 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.36 | 39964.51 | 2 | 1 | N-0 | 0.48 | 0.89 | N2 | 0.62737 | 0.07366 | N1 | 0.48884 | 0.73894 | N | 0.47678 | 0.89054 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 3.12 | 29313.64 | 0 | 1 | N-0 | 0.82 | 4.81 | N2 | 0.99086 | 0.53541 | N1 | 0.83354 | 1.6776 | N | 0.82053 | 4.8123 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 24.91 | 34661.38 | 2 | 2 | N-1 | 3.84 | 3.85 | N2 | 3.9135 | 0.75895 | N1 | 3.8423 | 3.8512 | N | 5.5561 | 62.7176 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 159.1 | 40211.29 | 2 | 2 | N-1 | 12.59 | 2.85 | N2 | 12.6602 | 2.85 | N1 | 12.5851 | 2.8505 | N | 21.9293 | 269.5558 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 3.99 | 33775.2 | 2 | 2 | N-1 | 1.18 | 1.75 | N2 | 1.2384 | 0.94062 | N1 | 1.1825 | 1.7495 | N | 1.3213 | 7.6127 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 30.81 | 36084.4 | 2 | 3 | N-1 | 4.9 | 0.81 | N2 | 5.0911 | 0.52753 | N1 | 4.8958 | 0.81351 | N | 6.1827 | 48.4923 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 297.27 | 39506.97 | 3 | 6 | N-1 | 25.18 | 1.9 | N2 | 26.1006 | 0.69737 | N1 | 25.1789 | 1.8983 | N | 26.5853 | 64.7223 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 100.54 | 34366.43 | 3 | 2 | N-1 | 9.57 | 5.42 | N2 | 9.588 | 5.4147 | N1 | 9.5737 | 5.4157 | N | 26.022 | 515.3907 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 33.99 | 34366.43 | 3 | 5 | N-1 | 6.01 | 0.74 | N2 | 6.2096 | 0.32706 | N1 | 6.0145 | 0.74308 | N | 6.5907 | 27.6473 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 40.35 | 34973.02 | 2 | 2 | N-1 | 5.27 | 1.56 | N2 | 5.3108 | 1.5642 | N1 | 5.2735 | 1.5649 | N | 9.1213 | 129.2682 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 20.41 | 6050 | 0 | 3 | N-1 | 3.58 | 2.35 | N2 | 3.5922 | 2.3434 | N1 | 3.582 | 2.3455 | N | 4.2514 | 168.4615 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 17.77 | 34214.81 | 2 | 3 | N-1 | 3.35 | 5.8 | N2 | 3.5604 | 1.0377 | N1 | 3.3545 | 5.8029 | N | 3.4212 | 8.7299 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 38.43 | 35050.92 | 3 | 3 | N-1 | 5.54 | 4.47 | N2 | 5.6638 | 0.42074 | N1 | 5.5396 | 4.4748 | N | 6.1849 | 29.9101 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 44.26 | 32755.83 | 2 | 1 | N-1 | 4.88 | 5.03 | N2 | 5.6122 | 1.259 | N1 | 4.8798 | 5.0273 | N | 6.6393 | 83.6206 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 4.9 | 33951.07 | 0 | 2 | N-1 | 1.3 | 2.03 | N2 | 1.3401 | 1.5081 | N1 | 1.3003 | 2.0293 | N | 1.5454 | 11.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 185.01 | 36345.95 | 2 | 2 | N-1 | 13.4 | 22.11 | N2 | 13.8139 | 0.99586 | N1 | 13.4038 | 22.1094 | N | 14.3119 | 57.5124 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 72 | 196.02 | 90000 | 3 | 2 | N-1 | 22.06 | 0.61 | N2 | 22.0648 | 0.61125 | N1 | 22.0646 | 0.6113 | N | 33.1491 | 149.0551 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 7 | 44548.95 | 0 | 1 | N-1 | 1.37 | 1.86 | N2 | 1.632 | 0.50146 | N1 | 1.3746 | 1.8576 | N | 1.4536 | 7.4614 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 23.8 | 32960.09 | 0 | 3 | N-0 | 3.66 | 3 | N2 | 3.8803 | 0.42984 | N1 | 3.6627 | 2.9968 | N | 3.6627 | 2.9968 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 373.04 | 36951.61 | 4 | 2 | N-1 | 8.56 | 2.24 | N2 | 8.5628 | 2.2357 | N1 | 8.5611 | 2.2362 | N | 14.8615 | 196.0751 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 584.48 | 90000 | 5 | 6 | N-1 | 11.87 | 0.6 | N2 | 11.8712 | 0.60019 | N1 | 11.8707 | 0.60028 | N | 14.522 | 35.9581 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 722.85 | 90000 | 6 | 6 | N-1 | 13.74 | 0.6 | N2 | 13.7689 | 0.59504 | N1 | 13.7396 | 0.59515 | N | 16.0958 | 32.1195 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 775.16 | 38534.2 | 5 | 9 | N-1 | 19.28 | 5.29 | N2 | 19.3611 | 0.78298 | N1 | 19.2776 | 5.2901 | N | 20.5242 | 53.5543 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 71.01 | 36249.54 | 2 | 2 | N-1 | 7.53 | 1.94 | N2 | 7.5776 | 1.9423 | N1 | 7.5289 | 1.9432 | N | 12.4237 | 160.4974 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 16.8 | 34906.04 | 2 | 3 | N-1 | 3.19 | 4.14 | N2 | 3.4303 | 0.8414 | N1 | 3.1906 | 4.1428 | N | 3.2555 | 6.936 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 32.9 | 34906.04 | 2 | 3 | N-1 | 5.09 | 0.64 | N2 | 5.3 | 0.4791 | N1 | 5.0944 | 0.64095 | N | 5.9714 | 38.6335 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 3.42 | 33891.4 | 2 | 2 | N-1 | 1.12 | 2.06 | N2 | 1.1425 | 1.3228 | N1 | 1.1152 | 2.0631 | N | 1.3304 | 10.7081 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 146.76 | 39506.97 | 3 | 4 | N-1 | 15.41 | 22.75 | N2 | 15.426 | 22.7365 | N1 | 15.4134 | 22.7489 | N | 94.3435 | 2050.7096 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 675.73 | 6050.12 | 4 | 4 | N-1 | 38.48 | 108.63 | N2 | 38.5936 | 108.5754 | N1 | 38.4761 | 108.6327 | N | 93.3247 | 9531.262 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 127.67 | 35530.24 | 2 | 2 | N-1 | 10.8 | 10.67 | N2 | 10.9582 | 1.8265 | N1 | 10.7963 | 10.6702 | N | 14.9879 | 150.8914 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 22.51 | 33997.2 | 2 | 2 | N-1 | 3.64 | 2.42 | N2 | 3.6822 | 0.95984 | N1 | 3.6421 | 2.4208 | N | 5.8678 | 79.3269 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 69.24 | 35530.24 | 2 | 4 | N-1 | 8.75 | 12.42 | N2 | 9.2938 | 1.1807 | N1 | 8.7453 | 12.4223 | N | 8.8821 | 19.3418 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 331.66 | 35546.44 | 3 | 2 | N-1 | 19.92 | 42.12 | N2 | 20.1109 | 1.1773 | N1 | 19.9165 | 42.1249 | N | 20.3052 | 67.6917 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 50.74 | 34841.54 | 3 | 4 | N-1 | 7.15 | 8.65 | N2 | 7.3974 | 0.99517 | N1 | 7.1472 | 8.6504 | N | 7.3042 | 15.7797 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 37.94 | 34841.54 | 0 | 2 | N-1 | 4.81 | 1.93 | N2 | 4.8261 | 1.9314 | N1 | 4.8148 | 1.9317 | N | 10.5127 | 182.4821 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 14.27 | 34841.54 | 1 | 3 | N-1 | 2.89 | 2.86 | N2 | 3.0979 | 0.8815 | N1 | 2.8914 | 2.8622 | N | 2.9539 | 7.4116 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 55.58 | 34084.58 | 2 | 4 | N-0 | 7.4 | 8.31 | N2 | 8.0476 | 1.0183 | N1 | 7.4035 | 8.3134 | N | 7.4034 | 8.3134 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 2.44 | 34084.58 | 2 | 4 | N-0 | 1.01 | 0.59 | N2 | 1.1206 | 0.07069 | N1 | 1.0057 | 0.59281 | N | 1.0056 | 0.59281 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 143.02 | 39506.97 | 2 | 2 | N-1 | 11.71 | 1.79 | N2 | 11.7799 | 1.785 | N1 | 11.7092 | 1.7859 | N | 16.181 | 147.4568 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 114.89 | 34746.88 | 2 | 2 | N-1 | 10.28 | 4.09 | N2 | 10.3404 | 4.0881 | N1 | 10.2777 | 4.0889 | N | 22.4306 | 386.6566 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 6.83 | 34746.88 | 0 | 1 | N-0 | 1.23 | 3.49 | N2 | 1.5906 | 0.19852 | N1 | 1.259 | 3.4759 | N | 1.225 | 3.4935 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 126 | 37279.21 | 2 | 4 | N-1 | 13.01 | 4.33 | N2 | 13.6506 | 1.6725 | N1 | 13.0108 | 4.3275 | N | 17.8495 | 156.2091 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 26.3 | 35914.09 | 2 | 4 | N-1 | 4.7 | 6.2 | N2 | 5.0276 | 1.3039 | N1 | 4.7011 | 6.2018 | N | 4.8351 | 11.666 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 9.1 | 32580.51 | 0 | 2 | N-1 | 1.95 | 1.79 | N2 | 1.9555 | 1.7915 | N1 | 1.9454 | 1.7925 | N | 2.1429 | 14.1689 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 8.37 | 32580.51 | 2 | 6 | N-1 | 2.58 | 0.75 | N2 | 2.7848 | 0.05401 | N1 | 2.5751 | 0.75043 | N | 2.5918 | 4.3476 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25MD130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 145 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 130 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 33.5 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 4.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 470.1 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 87.3 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 28.8 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 10.4 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 19.5 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 13 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 49.4 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 28.6 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 565.5 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 35.1 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 62.1 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 13.9 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 16.9 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 22.4 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 52 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 39.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 742.3 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 22.8 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 58.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2.5 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 26 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 23 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 40 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 78 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 10.4 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 104 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 32.6 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 10.9 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 579.8 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 11 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 407.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 10.4 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 184.5 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 45.6 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 30.9 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 61.8 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 32.2 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 150.1 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 484.7 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 210.6 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 210.6 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 10.3 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 13.3 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 135.3 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 5.3 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 34.4 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 8.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 53.4 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 26.9 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 147.1 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 158.6 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 2.5 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 5.8 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 46.3 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 295.5 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 7.4 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 57.2 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 552.1 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 186.7 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 63.1 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 74.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 37.9 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 33 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 71.4 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 82.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 9.1 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 343.6 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 364 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 13 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 44.2 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 692.8 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 1085.5 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1342.4 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1439.6 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 131.9 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 31.2 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 61.1 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 6.4 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 272.6 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 1254.9 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 237.1 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 41.8 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 128.6 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 615.9 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 94.2 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 70.5 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 26.5 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 103.2 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 4.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 265.6 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 213.4 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 12.7 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 234 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 48.8 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 16.9 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 15.6 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 145.01 | 36118.62 | 0 | 3 | N-1 | 12.31 | 15.79 | N2 | 12.3367 | 0.90801 | N1 | 12.3064 | 15.7854 | N | 13.6295 | 64.9584 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 130 | 6050 | 0 | 3 | N-1 | 11.53 | 8.57 | N2 | 11.5412 | 8.5676 | N1 | 11.5275 | 8.5709 | N | 15.3435 | 796.9876 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 33.49 | 34827.32 | 2 | 4 | N-1 | 5.6 | 1.64 | N2 | 5.8969 | 0.54237 | N1 | 5.5964 | 1.6417 | N | 6.9215 | 50.8133 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 4.63 | 33792.6 | 1 | 1 | N-0 | 3.17 | 14.76 | N2 | 3.9239 | 1.3394 | N1 | 3.1939 | 3.6463 | N | 3.1717 | 14.7556 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 470.11 | 90000 | 3 | 1 | N-1 | 33.92 | 0.35 | N2 | 38.6405 | 0.6977 | N1 | 33.9218 | 0.35391 | N | 66.6317 | 431.9175 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 87.32 | 34024.46 | 2 | 2 | N-1 | 8.61 | 2.71 | N2 | 8.6614 | 2.714 | N1 | 8.6072 | 2.7145 | N | 16.2765 | 256.6895 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 28.82 | 33835.17 | 0 | 2 | N-1 | 3.97 | 4.45 | N2 | 4.0317 | 0.97339 | N1 | 3.9742 | 4.4534 | N | 6.1936 | 79.9828 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 10.4 | 6050 | 2 | 2 | N-1 | 2.1 | 9.82 | N2 | 2.2182 | 3.8972 | N1 | 2.1049 | 9.8175 | N | 2.1259 | 30.2773 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 19.5 | 6050 | 2 | 2 | N-1 | 3.16 | 18.41 | N2 | 3.3075 | 7.3072 | N1 | 3.1552 | 18.4078 | N | 3.2375 | 56.77 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 13 | 39506.97 | 2 | 2 | N-1 | 2.62 | 1.11 | N2 | 2.6433 | 1.1101 | N1 | 2.619 | 1.1106 | N | 5.8622 | 91.7508 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 49.4 | 34429.94 | 2 | 1 | N-1 | 14.67 | 5.17 | N2 | 17.3858 | 1.6249 | N1 | 14.6738 | 5.171 | N | 17.828 | 167.6056 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 28.6 | 34429.94 | 0 | 1 | N-1 | 10.27 | 1.55 | N2 | 11.9751 | 3.12 | N1 | 10.2728 | 1.5488 | N | 13.2854 | 148.6851 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 565.5 | 37279.21 | 4 | 5 | N-1 | 36.29 | 6.42 | N2 | 36.6641 | 5.2735 | N1 | 36.2891 | 6.4191 | N | 51.3932 | 459.5527 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 35.09 | 35252.82 | 0 | 1 | N-1 | 3.86 | 1.83 | N2 | 4.5534 | 0.87788 | N1 | 3.8603 | 1.8345 | N | 5.2648 | 61.2339 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 62.07 | 36373.37 | 3 | 6 | N-1 | 9.28 | 0.79 | N2 | 9.642 | 0.28077 | N1 | 9.2759 | 0.78566 | N | 9.6604 | 23.2763 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 13.88 | 38166.21 | 0 | 2 | N-1 | 2.42 | 2.77 | N2 | 2.5258 | 1.3532 | N1 | 2.4158 | 2.7697 | N | 2.6025 | 10.6944 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 16.9 | 34357.34 | 3 | 3 | N-1 | 3.37 | 2.09 | N2 | 3.3951 | 0.36898 | N1 | 3.3684 | 2.0901 | N | 3.9474 | 26.273 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 22.43 | 34357.34 | 3 | 3 | N-0 | 3.73 | 2.43 | N2 | 3.9703 | 0.33328 | N1 | 3.7285 | 2.4301 | N | 3.7284 | 2.4301 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 52 | 34357.34 | 0 | 2 | N-1 | 5.7 | 4.87 | N2 | 5.8413 | 1.4932 | N1 | 5.7021 | 4.8689 | N | 9.2943 | 122.6893 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 39.2 | 33830.95 | 2 | 3 | N-1 | 5.4 | 5.42 | N2 | 5.8577 | 0.99455 | N1 | 5.4036 | 5.4174 | N | 5.4411 | 8.0117 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 742.34 | 39574.74 | 4 | 3 | N-1 | 38.2 | 24.05 | N2 | 38.2282 | 24.041 | N1 | 38.1955 | 24.0501 | N | 123.1085 | 2239.9986 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 22.83 | 37690.78 | 2 | 1 | N-1 | 3.25 | 0.76 | N2 | 3.749 | 1.5673 | N1 | 3.2462 | 0.76325 | N | 5.4542 | 76.9372 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 58.57 | 35546.67 | 2 | 2 | N-1 | 6.67 | 1.84 | N2 | 6.7124 | 1.8424 | N1 | 6.668 | 1.8434 | N | 11.2513 | 152.2581 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 2.55 | 34513.16 | 0 | 1 | N-1 | 0.76 | 1.08 | N2 | 0.90598 | 1.3018 | N1 | 0.75894 | 1.083 | N | 0.78993 | 5.5005 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 26 | 35460.24 | 0 | 2 | N-1 | 3.72 | 3.9 | N2 | 3.7786 | 0.79212 | N1 | 3.7245 | 3.8981 | N | 5.5747 | 65.0853 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 22.97 | 35460.24 | 2 | 2 | N-1 | 3.68 | 2.06 | N2 | 3.7128 | 0.49899 | N1 | 3.6775 | 2.0621 | N | 4.6734 | 41.23 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 40 | 34721.47 | 2 | 2 | N-1 | 5.21 | 6.2 | N2 | 5.27 | 1.2195 | N1 | 5.2057 | 6.2023 | N | 8.0741 | 100.7762 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 78 | 6050 | 2 | 2 | N-1 | 7.84 | 8.83 | N2 | 7.9903 | 3.8522 | N1 | 7.8393 | 8.8324 | N | 8.9419 | 318.3791 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 10.41 | 34432.4 | 2 | 3 | N-1 | 2.45 | 2.72 | N2 | 2.5695 | 1.6187 | N1 | 2.4528 | 2.72 | N | 2.6889 | 13.4998 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 104.03 | 36683.18 | 3 | 2 | N-1 | 9.52 | 8.73 | N2 | 9.6572 | 1.6544 | N1 | 9.522 | 8.7297 | N | 13.5032 | 136.5545 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 32.57 | 36353.07 | 2 | 2 | N-1 | 4.57 | 5.04 | N2 | 4.6285 | 0.89667 | N1 | 4.5693 | 5.0357 | N | 6.7063 | 74.0961 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 10.93 | 32848.83 | 0 | 1 | N-1 | 1.76 | 2.8 | N2 | 2.1374 | 0.31874 | N1 | 1.7629 | 2.8 | N | 1.9445 | 14.0596 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 579.81 | 90000 | 3 | 1 | N-1 | 38.78 | 0.28 | N2 | 44.1569 | 0.40164 | N1 | 38.7782 | 0.28095 | N | 71.0417 | 436.1873 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 11 | 38350 | 0 | 1 | N-1 | 1.88 | 0.58 | N2 | 2.2201 | 0.34332 | N1 | 1.8794 | 0.585 | N | 2.2612 | 20.1288 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 407.07 | 40649.71 | 2 | 4 | N-1 | 78.79 | 74.46 | N2 | 89.5484 | 1.4076 | N1 | 78.7927 | 74.4643 | N | 79.0624 | 87.9632 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 10.4 | 38350 | 0 | 1 | N-1 | 1.85 | 1.07 | N2 | 2.1429 | 0.27583 | N1 | 1.8517 | 1.0728 | N | 2.0955 | 17.1644 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 184.46 | 39149.41 | 2 | 2 | N-1 | 5.19 | 0.78 | N2 | 5.2144 | 0.7832 | N1 | 5.1859 | 0.78335 | N | 7.2634 | 67.5668 | 0 | 0.1 | 0 | 0 | 0 | 0
| 38 | 45.55 | 34247.59 | 2 | 3 | N-1 | 6.12 | 8.08 | N2 | 6.4813 | 1.1708 | N1 | 6.1212 | 8.0844 | N | 6.3352 | 18.8305 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 39 | 30.89 | 34693 | 2 | 5 | N-1 | 5.61 | 2.03 | N2 | 6.0045 | 1.4344 | N1 | 5.6098 | 2.026 | N | 5.7536 | 13.6857 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 61.76 | 35142.51 | 3 | 3 | N-1 | 7.51 | 7 | N2 | 7.6327 | 0.43617 | N1 | 7.5069 | 6.9989 | N | 8.0423 | 30.9588 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 32.23 | 40211.29 | 0 | 6 | N-1 | 5.85 | 0.37 | N2 | 5.8625 | 0.37401 | N1 | 5.8525 | 0.37435 | N | 6.8694 | 33.2816 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 150.15 | 36003.25 | 2 | 2 | N-1 | 12.13 | 3.21 | N2 | 12.207 | 3.2087 | N1 | 12.1343 | 3.2093 | N | 21.6112 | 303.4862 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 484.66 | 36329.98 | 3 | 2 | N-1 | 9.8 | 7.28 | N2 | 9.8297 | 1.1203 | N1 | 9.804 | 7.2763 | N | 11.0351 | 59.883 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 210.6 | 37364.49 | 1 | 2 | N-2 | 5.68 | 1.25 | N2 | 5.6821 | 1.2456 | N1 | 5.946 | 0.98501 | N | 8.8364 | 103.4109 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 210.6 | 37364.49 | 1 | 1 | N-1 | 4.87 | 0.77 | N2 | 5.6821 | 1.2456 | N1 | 4.8742 | 0.76862 | N | 7.2857 | 82.6642 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 10.29 | 35222.85 | 0 | 2 | N-1 | 2.1 | 2.2 | N2 | 2.1323 | 0.384 | N1 | 2.1049 | 2.2006 | N | 2.9281 | 31.554 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 13.27 | 33960.97 | 0 | 2 | N-1 | 2.49 | 0.89 | N2 | 2.5044 | 0.89178 | N1 | 2.4942 | 0.89223 | N | 4.6213 | 73.2846 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 135.28 | 36864.7 | 1 | 6 | N-1 | 15.52 | 12.04 | N2 | 16.3717 | 1.237 | N1 | 15.516 | 12.0401 | N | 18.1884 | 102.7274 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 5.32 | 32176.46 | 1 | 3 | N-1 | 1.59 | 1.59 | N2 | 1.6742 | 0.77135 | N1 | 1.5853 | 1.5944 | N | 1.6484 | 6.3492 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 34.42 | 37146.71 | 2 | 2 | N-1 | 4.76 | 1.07 | N2 | 4.7975 | 1.0716 | N1 | 4.7627 | 1.0721 | N | 7.4462 | 88.5539 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 8.66 | 38350 | 0 | 1 | N-1 | 1.59 | 1.41 | N2 | 1.9089 | 1.0279 | N1 | 1.5913 | 1.4103 | N | 1.8475 | 14.7773 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 53.41 | 38401.47 | 2 | 3 | N-1 | 6.88 | 7.61 | N2 | 7.1889 | 0.56697 | N1 | 6.8765 | 7.6063 | N | 8.0904 | 46.6274 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 26.89 | 34311.06 | 0 | 1 | N-1 | 3.31 | 2.9 | N2 | 3.8489 | 0.54926 | N1 | 3.3148 | 2.901 | N | 4.1704 | 45.1269 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 147.1 | 35530.24 | 1 | 2 | N-2 | 11.99 | 1.84 | N2 | 11.9862 | 1.8364 | N1 | 12.0137 | 4.5933 | N | 15.9766 | 154.16 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 158.6 | 35530.24 | 2 | 2 | N-1 | 12.43 | 12.95 | N2 | 12.5744 | 1.8994 | N1 | 12.4255 | 12.9542 | N | 16.6417 | 156.8764 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 2.52 | 39964.51 | 2 | 1 | N-0 | 0.71 | 1.65 | N2 | 0.91432 | 0.1368 | N1 | 0.71986 | 1.3723 | N | 0.70804 | 1.6539 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 5.79 | 29313.64 | 0 | 1 | N-1 | 1.23 | 2.1 | N2 | 1.4597 | 0.99433 | N1 | 1.2341 | 2.0977 | N | 1.2585 | 8.9372 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 46.27 | 34661.38 | 2 | 2 | N-1 | 5.72 | 7.15 | N2 | 5.7776 | 1.4095 | N1 | 5.7176 | 7.1522 | N | 9.0584 | 116.4756 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 295.46 | 40211.29 | 2 | 2 | N-1 | 18.73 | 5.29 | N2 | 18.8416 | 5.2928 | N1 | 18.7331 | 5.2938 | N | 36.6569 | 500.6037 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 7.41 | 33775.2 | 2 | 2 | N-1 | 1.76 | 3.25 | N2 | 1.8335 | 1.7469 | N1 | 1.7624 | 3.2491 | N | 2.046 | 14.1379 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 57.21 | 36084.4 | 2 | 3 | N-1 | 7.25 | 1.24 | N2 | 7.5244 | 0.97969 | N1 | 7.248 | 1.2433 | N | 9.8325 | 90.0571 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 552.07 | 39506.97 | 3 | 6 | N-1 | 37.45 | 3.53 | N2 | 38.7632 | 1.2951 | N1 | 37.4536 | 3.5255 | N | 40.4991 | 120.1986 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 186.72 | 34366.43 | 3 | 2 | N-1 | 14.27 | 10.06 | N2 | 14.2862 | 10.0559 | N1 | 14.2678 | 10.0578 | N | 45.2596 | 957.1542 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 63.13 | 34366.43 | 3 | 5 | N-1 | 8.9 | 1.08 | N2 | 9.1816 | 0.6074 | N1 | 8.9045 | 1.0762 | N | 10.139 | 51.3451 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 74.93 | 34973.02 | 2 | 2 | N-1 | 7.82 | 2.54 | N2 | 7.8661 | 2.5382 | N1 | 7.8161 | 2.5387 | N | 15.2332 | 240.0696 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 37.9 | 6050 | 0 | 3 | N-1 | 5.28 | 4.36 | N2 | 5.2936 | 4.3521 | N1 | 5.2829 | 4.3559 | N | 6.6838 | 312.857 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 33 | 34214.81 | 2 | 3 | N-1 | 5.05 | 10.78 | N2 | 5.2875 | 1.9272 | N1 | 5.046 | 10.7768 | N | 5.1861 | 16.2127 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 71.37 | 35050.92 | 3 | 3 | N-1 | 8.25 | 8.31 | N2 | 8.3743 | 0.78137 | N1 | 8.2485 | 8.3102 | N | 9.5752 | 55.5474 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 82.19 | 32755.83 | 2 | 1 | N-1 | 7.24 | 1.57 | N2 | 8.3124 | 2.338 | N1 | 7.2404 | 1.5679 | N | 10.893 | 155.2954 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 9.1 | 33951.07 | 0 | 2 | N-1 | 1.93 | 2.46 | N2 | 1.9755 | 0.26959 | N1 | 1.9268 | 2.4594 | N | 2.4333 | 22.151 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 343.59 | 36345.95 | 2 | 2 | N-1 | 20.13 | 25.67 | N2 | 20.5277 | 1.8495 | N1 | 20.1279 | 25.6719 | N | 22.1003 | 106.8087 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 364.04 | 90000 | 3 | 2 | N-1 | 32.78 | 0.25 | N2 | 32.7792 | 0.25217 | N1 | 32.779 | 0.25219 | N | 54.2931 | 276.8165 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 13 | 44548.95 | 0 | 1 | N-1 | 2.06 | 2.71 | N2 | 2.4156 | 0.93128 | N1 | 2.0556 | 2.7065 | N | 2.2715 | 13.8569 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 44.2 | 32960.09 | 0 | 3 | N-0 | 5.47 | 5.57 | N2 | 5.7544 | 0.79828 | N1 | 5.4678 | 5.5654 | N | 5.4677 | 5.5654 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 692.78 | 36951.61 | 4 | 2 | N-1 | 12.72 | 4.15 | N2 | 12.7253 | 4.152 | N1 | 12.7227 | 4.1529 | N | 24.8497 | 364.1395 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 1085.46 | 90000 | 5 | 6 | N-1 | 17.63 | 1.11 | N2 | 17.6265 | 1.1146 | N1 | 17.6259 | 1.1148 | N | 22.882 | 66.7794 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1342.43 | 90000 | 6 | 6 | N-1 | 20.41 | 1.11 | N2 | 20.449 | 1.1051 | N1 | 20.408 | 1.1053 | N | 25.0983 | 59.6505 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1439.57 | 38534.2 | 5 | 9 | N-1 | 28.76 | 1.45 | N2 | 28.7654 | 1.4541 | N1 | 28.7639 | 1.4545 | N | 31.3664 | 99.458 | 0 | 0 | 0 | 0 | 0 | 0
| 79 | 131.87 | 36249.54 | 2 | 2 | N-1 | 11.18 | 3.15 | N2 | 11.247 | 3.1514 | N1 | 11.1794 | 3.152 | N | 20.6339 | 298.0666 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 31.2 | 34906.04 | 2 | 3 | N-1 | 4.78 | 7.69 | N2 | 5.0913 | 1.5626 | N1 | 4.7821 | 7.6938 | N | 4.9186 | 12.8811 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 61.1 | 34906.04 | 2 | 3 | N-1 | 7.54 | 1.19 | N2 | 7.8335 | 0.88975 | N1 | 7.5418 | 1.1903 | N | 9.3702 | 71.748 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 6.36 | 33891.4 | 2 | 2 | N-1 | 1.66 | 1.64 | N2 | 1.6867 | 1.2479 | N1 | 1.6572 | 1.6422 | N | 2.0985 | 19.8864 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 272.56 | 39506.97 | 3 | 4 | N-1 | 23.21 | 42.25 | N2 | 23.2205 | 42.2249 | N1 | 23.2054 | 42.2479 | N | 170.2823 | 3808.4606 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 1254.93 | 6050.12 | 4 | 4 | N-1 | 57.45 | 201.75 | N2 | 57.6287 | 201.6399 | N1 | 57.4541 | 201.7464 | N | 160.1981 | 17700.9151 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 237.11 | 35530.24 | 2 | 2 | N-1 | 16.18 | 19.82 | N2 | 16.2872 | 3.3922 | N1 | 16.1838 | 19.8161 | N | 24.2966 | 280.227 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 41.81 | 33997.2 | 2 | 2 | N-1 | 5.4 | 1.78 | N2 | 5.4355 | 1.7826 | N1 | 5.3976 | 1.7834 | N | 9.7147 | 147.3214 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 128.58 | 35530.24 | 2 | 4 | N-1 | 13.05 | 1.1 | N2 | 13.7786 | 0.39151 | N1 | 13.0459 | 1.1038 | N | 13.4599 | 35.9205 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 615.95 | 35546.44 | 3 | 2 | N-1 | 29.88 | 2.19 | N2 | 29.9147 | 2.1863 | N1 | 29.8759 | 2.1879 | N | 31.1568 | 125.7132 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 94.23 | 34841.54 | 3 | 4 | N-1 | 10.72 | 15.15 | N2 | 10.9684 | 0.38536 | N1 | 10.7248 | 15.1529 | N | 11.0551 | 29.3051 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 70.46 | 34841.54 | 0 | 2 | N-1 | 7.14 | 3.59 | N2 | 7.1487 | 3.5868 | N1 | 7.1358 | 3.5875 | N | 17.9737 | 338.8953 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 26.5 | 34841.54 | 1 | 3 | N-1 | 4.32 | 5.32 | N2 | 4.5975 | 1.6371 | N1 | 4.323 | 5.3155 | N | 4.4786 | 13.7643 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 103.21 | 34084.58 | 2 | 4 | N-0 | 11.11 | 15.44 | N2 | 11.9567 | 1.8912 | N1 | 11.1087 | 15.4392 | N | 11.1086 | 15.4392 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 4.53 | 34084.58 | 2 | 4 | N-0 | 1.49 | 1.1 | N2 | 1.6468 | 0.13128 | N1 | 1.4882 | 1.1009 | N | 1.4882 | 1.1009 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 265.6 | 39506.97 | 2 | 2 | N-1 | 17.41 | 3.32 | N2 | 17.5144 | 3.315 | N1 | 17.4128 | 3.3166 | N | 26.2479 | 273.8483 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 213.36 | 34746.88 | 2 | 2 | N-1 | 15.3 | 7.59 | N2 | 15.3923 | 7.5922 | N1 | 15.3032 | 7.5936 | N | 38.3481 | 718.0765 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 12.68 | 34746.88 | 0 | 1 | N-0 | 1.85 | 6.49 | N2 | 2.3481 | 0.36868 | N1 | 1.8999 | 6.4552 | N | 1.8535 | 6.488 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 234 | 37279.21 | 2 | 4 | N-1 | 19.38 | 8.04 | N2 | 20.2677 | 3.1061 | N1 | 19.3816 | 8.0368 | N | 28.7086 | 290.1026 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 48.84 | 35914.09 | 2 | 4 | N-1 | 7.05 | 1.57 | N2 | 7.4601 | 1.3083 | N1 | 7.0475 | 1.5725 | N | 7.3337 | 21.6655 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 16.9 | 32580.51 | 0 | 2 | N-1 | 2.87 | 0.32 | N2 | 2.8819 | 0.32026 | N1 | 2.8715 | 0.32042 | N | 3.3429 | 26.3136 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 15.55 | 32580.51 | 2 | 6 | N-1 | 3.82 | 1.39 | N2 | 4.1244 | 0.1003 | N1 | 3.8233 | 1.3937 | N | 3.8917 | 8.0742 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25discrateL
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.047
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 9.56 | 12.14 | N2 | 9.5865 | 0.69847 | N1 | 9.5586 | 12.1426 | N | 10.5627 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 8.96 | 6.59 | N2 | 8.9703 | 6.5904 | N1 | 8.9576 | 6.593 | N | 11.8763 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.36 | 1.26 | N2 | 4.599 | 0.41721 | N1 | 4.3568 | 1.2629 | N | 5.3639 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.47 | 11.35 | N2 | 3.0765 | 1.0303 | N1 | 2.4947 | 2.8048 | N | 2.4733 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 26.44 | 0.27 | N2 | 30.112 | 0.5367 | N1 | 26.4402 | 0.27224 | N | 51.5091 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 6.69 | 2.09 | N2 | 6.7463 | 2.0877 | N1 | 6.6943 | 2.088 | N | 12.5746 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.1 | 3.43 | N2 | 3.1449 | 0.74876 | N1 | 3.0984 | 3.4257 | N | 4.7927 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.64 | 7.55 | N2 | 1.7313 | 2.9978 | N1 | 1.6399 | 7.5519 | N | 1.6543 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.45 | 14.16 | N2 | 2.5773 | 5.6209 | N1 | 2.4543 | 14.1599 | N | 2.5155 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.05 | 0.85 | N2 | 2.0719 | 0.85392 | N1 | 2.0478 | 0.85434 | N | 4.5302 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 11.42 | 3.98 | N2 | 13.548 | 1.6117 | N1 | 11.4152 | 3.9777 | N | 13.8075 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8 | 1.19 | N2 | 9.3332 | 2.4 | N1 | 7.9987 | 1.1914 | N | 10.288 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 28.16 | 4.94 | N2 | 28.4823 | 4.0565 | N1 | 28.1649 | 4.9378 | N | 39.7622 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.01 | 1.41 | N2 | 3.5495 | 0.6753 | N1 | 3.0102 | 1.4112 | N | 4.0756 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.21 | 1.45 | N2 | 7.5017 | 1.143 | N1 | 7.2074 | 1.4543 | N | 7.4953 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 1.88 | 2.13 | N2 | 1.9671 | 1.0409 | N1 | 1.8803 | 2.1305 | N | 2.0221 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.63 | 2.56 | N2 | 2.6535 | 1.3065 | N1 | 2.6274 | 2.5577 | N | 3.0629 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 2.9 | 1.87 | N2 | 3.0916 | 0.25637 | N1 | 2.8985 | 1.8693 | N | 2.8984 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.44 | 3.75 | N2 | 4.5483 | 1.1486 | N1 | 4.4384 | 3.7453 | N | 7.1881 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.2 | 4.17 | N2 | 4.558 | 0.76504 | N1 | 4.1978 | 4.1672 | N | 4.2252 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 29.65 | 18.5 | N2 | 29.6729 | 18.4931 | N1 | 29.6455 | 18.5001 | N | 94.9268 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.53 | 0.59 | N2 | 2.9305 | 1.3797 | N1 | 2.5346 | 0.58712 | N | 4.2183 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.19 | 1.42 | N2 | 5.232 | 1.4173 | N1 | 5.1891 | 1.418 | N | 8.6985 | 117.1216 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.6 | 0.83 | N2 | 0.71063 | 1.0014 | N1 | 0.59552 | 0.83304 | N | 0.61746 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 2.9 | 3 | N2 | 2.9486 | 0.60933 | N1 | 2.9049 | 2.9986 | N | 4.3152 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 2.87 | 1.59 | N2 | 2.9028 | 0.38384 | N1 | 2.8693 | 1.5862 | N | 3.6221 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.05 | 4.77 | N2 | 4.112 | 0.93808 | N1 | 4.0536 | 4.771 | N | 6.2466 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.1 | 6.79 | N2 | 6.2248 | 2.9632 | N1 | 6.0967 | 6.7941 | N | 6.9293 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 1.91 | 2.09 | N2 | 2.0038 | 1.2452 | N1 | 1.9095 | 2.0923 | N | 2.0892 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 7.4 | 6.72 | N2 | 7.5111 | 1.2726 | N1 | 7.4015 | 6.7152 | N | 10.4489 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.56 | 3.87 | N2 | 3.6138 | 0.68975 | N1 | 3.5602 | 3.8736 | N | 5.191 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.37 | 2.15 | N2 | 1.6661 | 0.24519 | N1 | 1.3738 | 2.1538 | N | 1.5112 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 30.22 | 0.22 | N2 | 34.4083 | 0.30895 | N1 | 30.2235 | 0.21612 | N | 54.9353 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.47 | 1.24 | N2 | 1.7398 | 0.26409 | N1 | 1.4691 | 1.2412 | N | 1.7549 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 61.33 | 57.28 | N2 | 69.8103 | 1.0828 | N1 | 61.3276 | 57.2802 | N | 61.5362 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.45 | 0.83 | N2 | 1.6795 | 1.1177 | N1 | 1.4464 | 0.82521 | N | 1.6271 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.04 | 4.55 | N2 | 4.0715 | 0.60246 | N1 | 4.0404 | 4.5481 | N | 5.6166 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 4.75 | 5.31 | N2 | 5.0451 | 1.7351 | N1 | 4.7544 | 5.3129 | N | 4.9162 | 14.485 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.36 | 1.56 | N2 | 4.6718 | 1.1034 | N1 | 4.3575 | 1.5584 | N | 4.4664 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 5.84 | 6.33 | N2 | 5.946 | 0.33551 | N1 | 5.8371 | 6.3276 | N | 6.2384 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.56 | 0.29 | N2 | 4.5663 | 0.2877 | N1 | 4.5564 | 0.28796 | N | 5.3259 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 9.43 | 2.47 | N2 | 9.4992 | 2.4682 | N1 | 9.43 | 2.4687 | N | 16.6971 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 7.64 | 5.6 | N2 | 7.6497 | 0.8618 | N1 | 7.6357 | 5.5972 | N | 8.5445 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.43 | 0.96 | N2 | 4.4346 | 0.95816 | N1 | 4.6276 | 3.6496 | N | 6.8147 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 3.8 | 0.59 | N2 | 4.4346 | 0.95816 | N1 | 3.8011 | 0.59124 | N | 5.6158 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.65 | 1.69 | N2 | 1.6718 | 0.29539 | N1 | 1.649 | 1.6928 | N | 2.2701 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 1.95 | 0.69 | N2 | 1.9603 | 0.68598 | N1 | 1.9502 | 0.68633 | N | 3.5746 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 12.04 | 9.26 | N2 | 12.7335 | 0.95152 | N1 | 12.0426 | 9.2616 | N | 14.0833 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.24 | 1.23 | N2 | 1.3086 | 0.59335 | N1 | 1.2365 | 1.2265 | N | 1.2834 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 3.71 | 0.82 | N2 | 3.7451 | 0.8243 | N1 | 3.7111 | 0.8247 | N | 5.761 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.24 | 1.77 | N2 | 1.4929 | 0.79071 | N1 | 1.2433 | 1.7704 | N | 1.4353 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.35 | 5.85 | N2 | 5.6024 | 0.43613 | N1 | 5.3491 | 5.851 | N | 6.2702 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.59 | 2.23 | N2 | 3.0031 | 0.42251 | N1 | 2.587 | 2.2316 | N | 3.2307 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 9.33 | 3.53 | N2 | 9.3275 | 1.4126 | N1 | 9.3252 | 3.5333 | N | 12.3555 | 118.5846 | 0 | 0.6 | 0 | 0 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 9.65 | 9.96 | N2 | 9.7843 | 1.461 | N1 | 9.6497 | 9.9648 | N | 12.8767 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.56 | 1.27 | N2 | 0.71849 | 0.10523 | N1 | 0.5654 | 1.0556 | N | 0.55502 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 0.96 | 1.61 | N2 | 1.1403 | 0.76487 | N1 | 0.96391 | 1.6136 | N | 0.98039 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.45 | 5.5 | N2 | 4.5062 | 1.0842 | N1 | 4.4504 | 5.5017 | N | 7.0066 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 14.55 | 4.07 | N2 | 14.6497 | 4.0714 | N1 | 14.5475 | 4.0722 | N | 28.3048 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.37 | 2.5 | N2 | 1.4322 | 1.3437 | N1 | 1.3739 | 2.4993 | N | 1.5903 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 5.64 | 1.16 | N2 | 5.8629 | 0.75361 | N1 | 5.638 | 1.1622 | N | 7.6121 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 29.06 | 2.71 | N2 | 30.115 | 0.99624 | N1 | 29.0648 | 2.7119 | N | 31.3875 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 11.08 | 7.74 | N2 | 11.1011 | 7.7353 | N1 | 11.0847 | 7.7367 | N | 34.9012 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 6.92 | 0.83 | N2 | 7.1484 | 0.46723 | N1 | 6.9249 | 0.82782 | N | 7.8606 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.08 | 1.95 | N2 | 6.1288 | 1.9525 | N1 | 6.0805 | 1.9529 | N | 11.7677 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.11 | 3.35 | N2 | 4.1238 | 3.3477 | N1 | 4.1133 | 3.3507 | N | 5.1782 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 3.92 | 8.29 | N2 | 4.1149 | 1.4824 | N1 | 3.9193 | 8.2898 | N | 4.0256 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.41 | 6.39 | N2 | 6.5217 | 0.60106 | N1 | 6.4144 | 6.3925 | N | 7.422 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 5.63 | 1.21 | N2 | 6.4745 | 1.7985 | N1 | 5.6337 | 1.2061 | N | 8.4218 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.51 | 1.89 | N2 | 1.545 | 1.0924 | N1 | 1.5054 | 1.8918 | N | 1.8886 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 15.62 | 19.75 | N2 | 15.9598 | 1.4226 | N1 | 15.6162 | 19.7476 | N | 17.117 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 25.55 | 0.19 | N2 | 25.5476 | 0.19398 | N1 | 25.5475 | 0.19399 | N | 42.0408 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.6 | 2.65 | N2 | 1.8817 | 0.71637 | N1 | 1.6021 | 2.6538 | N | 1.7639 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.25 | 4.28 | N2 | 4.4716 | 0.61406 | N1 | 4.246 | 4.2811 | N | 4.246 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 9.9 | 3.19 | N2 | 9.9034 | 3.1938 | N1 | 9.9012 | 3.1945 | N | 19.1913 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 13.73 | 0.86 | N2 | 13.7321 | 0.85741 | N1 | 13.7315 | 0.85754 | N | 17.7216 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 15.89 | 0.85 | N2 | 15.9301 | 0.85006 | N1 | 15.8901 | 0.85021 | N | 19.4526 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 22.34 | 7.56 | N2 | 22.3672 | 1.1185 | N1 | 22.3409 | 7.5573 | N | 24.3136 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 8.69 | 2.42 | N2 | 8.7539 | 2.4242 | N1 | 8.6894 | 2.4246 | N | 15.9403 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 3.72 | 5.92 | N2 | 3.9626 | 1.202 | N1 | 3.7152 | 5.9183 | N | 3.8188 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 5.87 | 0.92 | N2 | 6.103 | 0.68442 | N1 | 5.8655 | 0.91564 | N | 7.2583 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.3 | 1.26 | N2 | 1.323 | 0.95993 | N1 | 1.2969 | 1.2632 | N | 1.6298 | 15.2973 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 18.02 | 32.5 | N2 | 18.0374 | 32.4807 | N1 | 18.0235 | 32.4984 | N | 131.1206 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 44.59 | 155.19 | N2 | 44.7476 | 155.1076 | N1 | 44.585 | 155.1895 | N | 123.574 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 12.56 | 15.24 | N2 | 12.6668 | 2.6094 | N1 | 12.5612 | 15.2431 | N | 18.7843 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.2 | 1.37 | N2 | 4.2404 | 1.3712 | N1 | 4.2035 | 1.3719 | N | 7.5094 | 113.3242 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 10.13 | 0.85 | N2 | 10.72 | 0.30116 | N1 | 10.134 | 0.84904 | N | 10.4375 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 23.19 | 1.68 | N2 | 23.226 | 1.6818 | N1 | 23.194 | 1.683 | N | 24.1393 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 8.32 | 12.36 | N2 | 8.5359 | 0.29643 | N1 | 8.3246 | 12.3577 | N | 8.576 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 5.55 | 2.76 | N2 | 5.5627 | 2.7591 | N1 | 5.5506 | 2.7596 | N | 13.8715 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.36 | 4.09 | N2 | 3.579 | 1.2593 | N1 | 3.3584 | 4.0889 | N | 3.4761 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 8.62 | 11.88 | N2 | 9.2947 | 1.4548 | N1 | 8.619 | 11.8764 | N | 8.6189 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.16 | 0.85 | N2 | 1.2875 | 0.10098 | N1 | 1.1605 | 0.84687 | N | 1.1604 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 13.52 | 2.55 | N2 | 13.6195 | 2.55 | N1 | 13.5237 | 2.5513 | N | 20.2916 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 11.89 | 5.84 | N2 | 11.9714 | 5.8401 | N1 | 11.887 | 5.8412 | N | 29.5877 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.44 | 4.99 | N2 | 1.8294 | 0.2836 | N1 | 1.4793 | 4.9655 | N | 1.4421 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 15.05 | 6.18 | N2 | 15.7584 | 2.3893 | N1 | 15.0452 | 6.1822 | N | 22.2019 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.48 | 1.21 | N2 | 5.807 | 1.0064 | N1 | 5.4769 | 1.2096 | N | 5.6899 | 16.6658 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.24 | 1.3 | N2 | 2.252 | 1.2977 | N1 | 2.2418 | 1.2984 | N | 2.5934 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 2.97 | 1.07 | N2 | 3.2077 | 0.07716 | N1 | 2.972 | 1.072 | N | 3.0235 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25discrateH
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.064
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 11.21 | 12.14 | N2 | 11.3149 | 0.69847 | N1 | 11.209 | 12.1426 | N | 12.1472 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 10.57 | 6.59 | N2 | 10.5844 | 6.5904 | N1 | 10.5717 | 6.593 | N | 13.3539 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 5.13 | 1.26 | N2 | 5.4122 | 0.41721 | N1 | 5.1331 | 1.2629 | N | 6.0838 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.84 | 11.35 | N2 | 3.5985 | 1.0303 | N1 | 2.9129 | 11.3505 | N | 2.8389 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 30.97 | 5.64 | N2 | 35.286 | 0.5367 | N1 | 30.9706 | 5.638 | N | 55.2168 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.86 | 10.67 | N2 | 7.926 | 2.3893 | N1 | 7.8645 | 10.6702 | N | 13.6242 | 197.4535 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.64 | 3.43 | N2 | 3.7051 | 0.74876 | N1 | 3.6356 | 3.4257 | N | 5.2805 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-0 | 1.92 | 23.29 | N2 | 2.0311 | 2.9978 | N1 | 1.9235 | 23.2903 | N | 1.9234 | 23.2903 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.88 | 14.16 | N2 | 3.0251 | 5.6209 | N1 | 2.8776 | 14.1599 | N | 2.9175 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.41 | 0.85 | N2 | 2.4285 | 0.85392 | N1 | 2.4077 | 0.85434 | N | 4.8405 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 13.43 | 11.85 | N2 | 15.9318 | 1.6117 | N1 | 13.4314 | 11.846 | N | 15.4756 | 128.9274 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 9.43 | 1.19 | N2 | 10.9886 | 2.4 | N1 | 9.4329 | 1.1914 | N | 11.4216 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 33.21 | 4.94 | N2 | 33.5551 | 4.0565 | N1 | 33.2113 | 4.9378 | N | 44.5542 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.54 | 1.41 | N2 | 4.1832 | 0.6753 | N1 | 3.5409 | 1.4112 | N | 4.507 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 8.5 | 1.45 | N2 | 8.8351 | 1.143 | N1 | 8.4983 | 1.4543 | N | 8.7296 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.2 | 3.35 | N2 | 2.3113 | 1.0409 | N1 | 2.2001 | 3.3518 | N | 2.3282 | 8.2264 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 3.08 | 2.56 | N2 | 3.1145 | 1.3065 | N1 | 3.0823 | 2.5577 | N | 3.4867 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.41 | 1.87 | N2 | 3.6381 | 0.25637 | N1 | 3.4063 | 1.8693 | N | 3.4062 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 5.22 | 3.75 | N2 | 5.3598 | 1.1486 | N1 | 5.2158 | 3.7453 | N | 7.8992 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.93 | 4.17 | N2 | 5.3616 | 0.76504 | N1 | 4.9265 | 4.1672 | N | 4.9466 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 34.84 | 18.5 | N2 | 34.8685 | 18.4931 | N1 | 34.8412 | 18.5001 | N | 99.7243 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.98 | 0.59 | N2 | 3.4367 | 1.3797 | N1 | 2.9846 | 0.58712 | N | 4.5704 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 6.08 | 6.98 | N2 | 6.1475 | 1.4173 | N1 | 6.0757 | 6.985 | N | 9.5111 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.69 | 0.83 | N2 | 0.82779 | 1.0014 | N1 | 0.6944 | 0.83304 | N | 0.69901 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.41 | 3 | N2 | 3.4739 | 0.60933 | N1 | 3.4088 | 2.9986 | N | 4.7721 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.37 | 1.59 | N2 | 3.4108 | 0.38384 | N1 | 3.373 | 1.5862 | N | 4.0684 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.75 | 4.77 | N2 | 4.8317 | 0.93808 | N1 | 4.7507 | 4.771 | N | 6.8831 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 7.18 | 6.79 | N2 | 7.3222 | 2.9632 | N1 | 7.1837 | 6.7941 | N | 7.9056 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.24 | 3.5 | N2 | 2.3483 | 1.2452 | N1 | 2.2364 | 3.504 | N | 2.3982 | 10.3845 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.68 | 6.72 | N2 | 8.8485 | 1.2726 | N1 | 8.6848 | 6.7152 | N | 11.6303 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 4.17 | 3.87 | N2 | 4.2463 | 0.68975 | N1 | 4.173 | 3.8736 | N | 5.7491 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.61 | 2.15 | N2 | 1.9616 | 0.24519 | N1 | 1.6057 | 2.1538 | N | 1.7163 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 35.42 | 0.22 | N2 | 40.325 | 0.30895 | N1 | 35.4214 | 0.21612 | N | 59.1796 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.72 | 2.06 | N2 | 2.0483 | 0.26409 | N1 | 1.7206 | 2.0573 | N | 1.9609 | 15.4837 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 71.51 | 57.28 | N2 | 81.747 | 1.0828 | N1 | 71.5137 | 57.2802 | N | 71.6877 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.7 | 2.11 | N2 | 1.971 | 1.1177 | N1 | 1.6975 | 2.1133 | N | 1.8259 | 13.2034 | 0 | 0 | 0 | 0 | 0.1 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.72 | 4.55 | N2 | 4.7767 | 0.60246 | N1 | 4.7211 | 4.5481 | N | 6.2461 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.56 | 8.66 | N2 | 5.9296 | 1.7351 | N1 | 5.5622 | 8.6578 | N | 5.7104 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 5.13 | 1.56 | N2 | 5.4947 | 1.1034 | N1 | 5.1326 | 1.5584 | N | 5.2047 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.85 | 6.33 | N2 | 6.9995 | 1.547 | N1 | 6.8464 | 6.3276 | N | 7.2089 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 5.38 | 0.49 | N2 | 5.3886 | 0.49017 | N1 | 5.3787 | 0.49095 | N | 6.1034 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 11.11 | 2.83 | N2 | 11.1641 | 2.8252 | N1 | 11.1075 | 2.8266 | N | 18.1832 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.92 | 7.62 | N2 | 8.9958 | 3.1538 | N1 | 8.9231 | 7.6165 | N | 9.7478 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 5.2 | 0.96 | N2 | 5.201 | 0.95816 | N1 | 5.4111 | 3.6496 | N | 7.4906 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.47 | 0.59 | N2 | 5.201 | 0.95816 | N1 | 4.4727 | 0.59124 | N | 6.1782 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.93 | 1.69 | N2 | 1.9678 | 0.29539 | N1 | 1.9337 | 1.6928 | N | 2.5231 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.3 | 0.69 | N2 | 2.3062 | 0.68598 | N1 | 2.2962 | 0.68633 | N | 3.872 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 14.16 | 9.26 | N2 | 14.9994 | 0.95152 | N1 | 14.1571 | 9.2616 | N | 16.1012 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.45 | 2.17 | N2 | 1.5332 | 0.59335 | N1 | 1.4473 | 2.1674 | N | 1.4833 | 4.884 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.37 | 0.82 | N2 | 4.3999 | 0.8243 | N1 | 4.3712 | 0.8247 | N | 6.3392 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.45 | 1.77 | N2 | 1.749 | 1.5594 | N1 | 1.4522 | 1.7704 | N | 1.6123 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 6.27 | 5.85 | N2 | 6.5929 | 0.43613 | N1 | 6.2706 | 5.851 | N | 7.1496 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 3.04 | 2.23 | N2 | 3.5396 | 0.42251 | N1 | 3.0367 | 2.2316 | N | 3.5947 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.91 | 14.48 | N2 | 10.9691 | 1.4126 | N1 | 10.9075 | 14.4819 | N | 13.8153 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 11.32 | 9.96 | N2 | 11.5063 | 1.461 | N1 | 11.3174 | 9.9648 | N | 14.4159 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.64 | 1.27 | N2 | 0.8403 | 0.10523 | N1 | 0.6556 | 1.0556 | N | 0.64179 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-0 | 1.12 | 6.87 | N2 | 1.3376 | 0.76487 | N1 | 1.1261 | 1.6136 | N | 1.1175 | 6.8747 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 5.21 | 5.5 | N2 | 5.295 | 1.0842 | N1 | 5.2143 | 5.5017 | N | 7.7052 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 17.13 | 4.07 | N2 | 17.2121 | 4.0714 | N1 | 17.129 | 4.0722 | N | 30.6001 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.6 | 2.5 | N2 | 1.6737 | 1.3437 | N1 | 1.6027 | 2.4993 | N | 1.8071 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.65 | 1.16 | N2 | 6.8974 | 0.75361 | N1 | 6.6451 | 1.1622 | N | 8.5311 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 34.29 | 2.71 | N2 | 35.5062 | 0.99624 | N1 | 34.2939 | 2.7119 | N | 36.3939 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 13.03 | 7.74 | N2 | 13.0427 | 7.7353 | N1 | 13.0263 | 7.7367 | N | 36.62 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 8.17 | 1.06 | N2 | 8.4206 | 0.46723 | N1 | 8.1674 | 1.0615 | N | 9.0326 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 7.16 | 2.24 | N2 | 7.1994 | 2.2345 | N1 | 7.1595 | 2.2356 | N | 12.7192 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.85 | 3.35 | N2 | 4.8634 | 3.3477 | N1 | 4.8529 | 3.3507 | N | 5.8503 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.57 | 8.29 | N2 | 4.8347 | 1.4824 | N1 | 4.572 | 8.2898 | N | 4.6717 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 7.53 | 6.39 | N2 | 7.6779 | 0.60106 | N1 | 7.5274 | 6.3925 | N | 8.4866 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.63 | 7.18 | N2 | 7.6089 | 1.7985 | N1 | 6.6298 | 7.1819 | N | 9.2217 | 119.458 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.76 | 1.89 | N2 | 1.8131 | 1.0924 | N1 | 1.7633 | 1.8918 | N | 2.1225 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 18.29 | 19.75 | N2 | 18.7783 | 1.4226 | N1 | 18.2851 | 19.7476 | N | 19.6462 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 29.94 | 0.19 | N2 | 29.9416 | 0.19398 | N1 | 29.9415 | 0.19399 | N | 45.9746 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.87 | 2.65 | N2 | 2.2118 | 0.71637 | N1 | 1.8667 | 2.6538 | N | 1.993 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.99 | 4.28 | N2 | 5.2747 | 0.61406 | N1 | 4.9875 | 4.2811 | N | 4.9875 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 11.62 | 3.19 | N2 | 11.6271 | 3.1938 | N1 | 11.6249 | 3.1945 | N | 20.7359 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 16.1 | 0.86 | N2 | 16.1033 | 0.85741 | N1 | 16.1028 | 0.85754 | N | 20.0039 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 18.65 | 0.85 | N2 | 18.6808 | 0.85006 | N1 | 18.6499 | 0.85021 | N | 22.1186 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 26.26 | 7.56 | N2 | 26.3176 | 1.1185 | N1 | 26.26 | 7.5573 | N | 28.1082 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 10.23 | 2.42 | N2 | 10.2872 | 2.4242 | N1 | 10.2343 | 2.4246 | N | 17.3075 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.35 | 5.92 | N2 | 4.6571 | 1.202 | N1 | 4.345 | 5.9183 | N | 4.4422 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.92 | 0.92 | N2 | 7.1814 | 0.68442 | N1 | 6.9154 | 0.91564 | N | 8.2167 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.51 | 2.95 | N2 | 1.5441 | 1.8897 | N1 | 1.5116 | 2.9473 | N | 1.8265 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 21.01 | 32.5 | N2 | 21.0288 | 32.4807 | N1 | 21.0149 | 32.4984 | N | 133.8914 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 52.44 | 155.19 | N2 | 52.5731 | 155.1076 | N1 | 52.4408 | 155.1895 | N | 130.9804 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 14.72 | 15.24 | N2 | 14.8914 | 2.6094 | N1 | 14.7166 | 15.2431 | N | 20.777 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.94 | 3.46 | N2 | 4.9804 | 1.3712 | N1 | 4.938 | 3.4583 | N | 8.1642 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.94 | 17.75 | N2 | 12.6283 | 0.30116 | N1 | 11.9368 | 17.7462 | N | 12.1416 | 27.6312 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 27.23 | 60.18 | N2 | 27.3779 | 1.6818 | N1 | 27.2271 | 60.1784 | N | 27.837 | 96.7024 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.75 | 12.36 | N2 | 10.0507 | 1.4217 | N1 | 9.7465 | 12.3577 | N | 9.979 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.54 | 2.76 | N2 | 6.5474 | 2.7591 | N1 | 6.5353 | 2.7596 | N | 14.735 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.94 | 4.09 | N2 | 4.2047 | 1.2593 | N1 | 3.936 | 4.0889 | N | 4.0339 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 10.1 | 11.88 | N2 | 10.9423 | 1.4548 | N1 | 10.0992 | 11.8764 | N | 10.0991 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.36 | 0.85 | N2 | 1.5114 | 0.10098 | N1 | 1.3614 | 0.84687 | N | 1.3613 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 15.93 | 2.55 | N2 | 16.0111 | 2.55 | N1 | 15.9331 | 2.5513 | N | 22.435 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 13.98 | 5.84 | N2 | 14.0537 | 5.8401 | N1 | 13.9849 | 5.8412 | N | 31.4498 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.67 | 4.99 | N2 | 2.1543 | 0.2836 | N1 | 1.7116 | 4.9655 | N | 1.6676 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 17.72 | 6.18 | N2 | 18.5529 | 2.3893 | N1 | 17.7169 | 6.1822 | N | 24.704 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 6.41 | 8.86 | N2 | 6.8324 | 1.8627 | N1 | 6.4088 | 8.8597 | N | 6.6065 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.64 | 1.3 | N2 | 2.6473 | 1.2977 | N1 | 2.6372 | 1.2984 | N | 2.9405 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.5 | 1.07 | N2 | 3.7799 | 0.71611 | N1 | 3.5 | 1.072 | N | 3.5305 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25failrate90
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.005013
failures_per_annum_per_100km_oh_line | 0.2611
failures_per_annum_per_100km_ug_cable | 0.0535
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.32 | 10.91 | N2 | 10.4294 | 0.61217 | N1 | 10.324 | 10.9096 | N | 11.1581 | 44.9288 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 7.49 | N2 | 9.7554 | 7.4801 | N1 | 9.7451 | 7.4862 | N | 12.2284 | 551.4497 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.73 | 1.12 | N2 | 4.9948 | 0.37235 | N1 | 4.7325 | 1.1188 | N | 5.5794 | 35.1432 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.61 | 10.22 | N2 | 3.3127 | 0.92448 | N1 | 2.6768 | 10.2158 | N | 2.6081 | 10.2158 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.65 | 5.07 | N2 | 32.6575 | 0.46819 | N1 | 28.6533 | 5.0694 | N | 50.3209 | 298.7395 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.25 | 9.6 | N2 | 7.3124 | 2.1154 | N1 | 7.2453 | 9.5967 | N | 12.4144 | 177.6595 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.35 | 3.08 | N2 | 3.4136 | 0.66403 | N1 | 3.349 | 3.081 | N | 4.8219 | 55.358 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-0 | 1.77 | 20.96 | N2 | 1.8731 | 2.6831 | N1 | 1.7706 | 20.9555 | N | 1.7705 | 20.9555 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.65 | 12.74 | N2 | 2.7902 | 5.0308 | N1 | 2.6519 | 12.7406 | N | 2.6847 | 39.2915 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.22 | 0.76 | N2 | 2.2396 | 0.75605 | N1 | 2.219 | 0.75639 | N | 4.4014 | 63.5028 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.37 | 10.64 | N2 | 14.6941 | 1.4126 | N1 | 12.3742 | 10.6412 | N | 14.1713 | 116.0381 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.7 | 1.07 | N2 | 10.1211 | 2.1521 | N1 | 8.6951 | 1.0723 | N | 10.4421 | 102.9398 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.63 | 4.42 | N2 | 30.9576 | 3.6005 | N1 | 30.6285 | 4.4176 | N | 40.784 | 317.6758 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.26 | 3.09 | N2 | 3.8545 | 0.59887 | N1 | 3.2624 | 3.095 | N | 4.1182 | 42.3943 | 0 | 0 | 0 | 0 | 0.3 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.84 | 1.29 | N2 | 8.1513 | 1.0163 | N1 | 7.8364 | 1.2943 | N | 8.0359 | 16.0834 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.03 | 3.02 | N2 | 2.1286 | 0.93539 | N1 | 2.0252 | 3.0155 | N | 2.1392 | 7.4015 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.84 | 2.3 | N2 | 2.872 | 1.1684 | N1 | 2.8407 | 2.2999 | N | 3.1998 | 18.1768 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.14 | 1.68 | N2 | 3.356 | 0.29093 | N1 | 3.1402 | 1.6809 | N | 3.1401 | 1.6809 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.81 | 3.37 | N2 | 4.9386 | 1.0186 | N1 | 4.8056 | 3.3676 | N | 7.2104 | 84.9159 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.54 | 3.74 | N2 | 4.9472 | 0.68091 | N1 | 4.5404 | 3.7445 | N | 4.5574 | 5.5396 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.12 | 16.57 | N2 | 32.1388 | 16.5625 | N1 | 32.1166 | 16.5681 | N | 90.4205 | 1549.8022 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.75 | 0.53 | N2 | 3.1696 | 1.2215 | N1 | 2.7521 | 0.52842 | N | 4.1654 | 53.2642 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.6 | 6.28 | N2 | 5.6719 | 1.2548 | N1 | 5.598 | 6.2822 | N | 8.6784 | 105.3803 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.75 | N2 | 0.76093 | 0.90003 | N1 | 0.63915 | 0.74977 | N | 0.64081 | 3.8081 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.14 | 2.7 | N2 | 3.2006 | 0.54037 | N1 | 3.1401 | 2.6969 | N | 4.3599 | 45.047 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.11 | 3.3 | N2 | 3.1472 | 0.33983 | N1 | 3.109 | 3.2982 | N | 3.7268 | 28.5357 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.38 | 4.29 | N2 | 4.458 | 0.83054 | N1 | 4.3777 | 4.2909 | N | 6.2877 | 69.7488 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.62 | 6.11 | N2 | 6.7575 | 2.6236 | N1 | 6.6246 | 6.1094 | N | 7.2582 | 220.3571 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.06 | 3.15 | N2 | 2.1653 | 1.1191 | N1 | 2.0596 | 3.1511 | N | 2.2034 | 9.3397 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8 | 6.04 | N2 | 8.1582 | 1.1282 | N1 | 8.0049 | 6.0377 | N | 10.6404 | 94.5097 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.85 | 3.48 | N2 | 3.918 | 0.61067 | N1 | 3.8455 | 3.4839 | N | 5.2556 | 51.2829 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.48 | 1.94 | N2 | 1.8069 | 0.21923 | N1 | 1.4784 | 1.9385 | N | 1.5741 | 9.734 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.19 | N2 | 37.3226 | 0.26954 | N1 | 32.7863 | 0.19424 | N | 53.9816 | 301.6933 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.58 | 1.85 | N2 | 1.8867 | 0.2342 | N1 | 1.5842 | 1.8517 | N | 1.7944 | 13.9359 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.12 | 51.45 | N2 | 75.6953 | 0.96235 | N1 | 66.1163 | 51.4474 | N | 66.2654 | 60.7883 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.56 | 1.9 | N2 | 1.8147 | 1.0031 | N1 | 1.5628 | 1.9021 | N | 1.6718 | 11.8835 | 0 | 0 | 0 | 0 | 0.1 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.36 | 4.09 | N2 | 4.4144 | 0.53145 | N1 | 4.3561 | 4.0926 | N | 5.7212 | 46.7724 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.12 | 7.78 | N2 | 5.4707 | 1.5512 | N1 | 5.1231 | 7.7818 | N | 5.2553 | 13.0237 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.73 | 1.39 | N2 | 5.0696 | 1.0132 | N1 | 4.7321 | 1.3949 | N | 4.7914 | 9.4589 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.31 | 5.69 | N2 | 6.4572 | 1.3825 | N1 | 6.3095 | 5.6861 | N | 6.6299 | 21.4132 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.42 | N2 | 4.9658 | 0.42057 | N1 | 4.9577 | 0.4212 | N | 5.6027 | 22.9947 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.24 | 2.5 | N2 | 10.3006 | 2.5013 | N1 | 10.2406 | 2.5024 | N | 16.5813 | 210.0468 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.24 | 6.85 | N2 | 8.299 | 4.1633 | N1 | 8.24 | 6.8502 | N | 8.9655 | 41.4532 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.85 | N2 | 4.8061 | 0.84523 | N1 | 4.9986 | 3.2623 | N | 6.8483 | 71.5907 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.53 | N2 | 4.8061 | 0.84523 | N1 | 4.1289 | 0.53214 | N | 5.6509 | 57.2309 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.78 | 2.59 | N2 | 1.8124 | 0.26196 | N1 | 1.7804 | 2.5895 | N | 2.3069 | 21.8393 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.61 | N2 | 2.124 | 0.60836 | N1 | 2.1159 | 0.60865 | N | 3.527 | 50.7223 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.05 | 8.33 | N2 | 13.8437 | 0.84024 | N1 | 13.049 | 8.3288 | N | 14.7804 | 70.991 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.33 | 1.95 | N2 | 1.4135 | 0.53321 | N1 | 1.3328 | 1.9493 | N | 1.364 | 4.3927 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.03 | 0.73 | N2 | 4.0595 | 0.7298 | N1 | 4.0303 | 0.73013 | N | 5.7896 | 61.2896 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.34 | 1.59 | N2 | 1.6097 | 1.4015 | N1 | 1.337 | 1.5934 | N | 1.4764 | 10.2308 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.78 | 5.26 | N2 | 6.0844 | 0.38441 | N1 | 5.7781 | 5.2578 | N | 6.5626 | 32.2568 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.8 | 2.01 | N2 | 3.2615 | 0.37468 | N1 | 2.7975 | 2.0085 | N | 3.2875 | 31.2429 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.05 | 13.03 | N2 | 10.1225 | 1.2506 | N1 | 10.0483 | 13.0268 | N | 12.647 | 106.6962 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.43 | 8.96 | N2 | 10.6183 | 1.2935 | N1 | 10.4303 | 8.9598 | N | 13.1996 | 108.5731 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.59 | 1.15 | N2 | 0.77411 | 0.09292 | N1 | 0.60337 | 0.9501 | N | 0.59043 | 1.145 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-0 | 1.03 | 6.19 | N2 | 1.2313 | 0.68739 | N1 | 1.0367 | 1.4523 | N | 1.0254 | 6.1875 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.8 | 4.95 | N2 | 4.8855 | 0.95992 | N1 | 4.8048 | 4.9482 | N | 7.0366 | 80.6146 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.79 | 3.65 | N2 | 15.8821 | 3.6489 | N1 | 15.7934 | 3.6496 | N | 27.874 | 346.4715 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.48 | 2.25 | N2 | 1.5425 | 1.2074 | N1 | 1.476 | 2.2487 | N | 1.6581 | 9.785 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.13 | 1.02 | N2 | 6.3653 | 0.67199 | N1 | 6.127 | 1.025 | N | 7.8111 | 62.3062 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.63 | 2.43 | N2 | 32.7666 | 0.89033 | N1 | 31.6284 | 2.4313 | N | 33.482 | 83.0897 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.01 | 6.93 | N2 | 12.0209 | 6.9304 | N1 | 12.0076 | 6.9316 | N | 33.2047 | 662.4489 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.53 | 0.93 | N2 | 7.7698 | 0.41334 | N1 | 7.5313 | 0.93129 | N | 8.2991 | 35.4972 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.6 | 1.98 | N2 | 6.6419 | 1.9784 | N1 | 6.6002 | 1.9793 | N | 11.5856 | 166.1567 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.47 | 2.94 | N2 | 4.4817 | 2.9361 | N1 | 4.4732 | 2.9385 | N | 5.3609 | 216.4729 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.21 | 7.45 | N2 | 4.4603 | 1.3785 | N1 | 4.2101 | 7.4533 | N | 4.2988 | 11.2145 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.94 | 5.74 | N2 | 7.0841 | 0.52562 | N1 | 6.9376 | 5.742 | N | 7.7933 | 38.4251 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.11 | 6.44 | N2 | 7.0206 | 1.5923 | N1 | 6.1082 | 6.441 | N | 8.4179 | 107.5138 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.62 | 1.7 | N2 | 1.6693 | 0.98041 | N1 | 1.6239 | 1.702 | N | 1.9437 | 15.3311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.85 | 17.76 | N2 | 17.3295 | 1.2272 | N1 | 16.8484 | 17.7564 | N | 18.0529 | 73.914 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.71 | 0.17 | N2 | 27.7125 | 0.16923 | N1 | 27.7123 | 0.16924 | N | 42.0467 | 191.4425 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.72 | 2.39 | N2 | 2.037 | 0.64375 | N1 | 1.718 | 2.3885 | N | 1.8266 | 9.5936 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.59 | 3.85 | N2 | 4.8612 | 0.5449 | N1 | 4.5949 | 3.8477 | N | 4.5949 | 3.8477 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.73 | 2.84 | N2 | 10.7353 | 2.8402 | N1 | 10.7335 | 2.8407 | N | 18.9103 | 252.0714 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.89 | 0.79 | N2 | 14.8879 | 0.79186 | N1 | 14.8874 | 0.79203 | N | 18.3802 | 46.2006 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.24 | 0.8 | N2 | 17.2723 | 0.79518 | N1 | 17.237 | 0.79538 | N | 20.3493 | 41.2639 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.24 | 6.77 | N2 | 24.3085 | 0.97275 | N1 | 24.2421 | 6.7724 | N | 25.8872 | 68.8151 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.44 | 2.46 | N2 | 9.4914 | 2.4566 | N1 | 9.4355 | 2.4577 | N | 15.7758 | 206.2961 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4 | 5.32 | N2 | 4.2965 | 1.0751 | N1 | 4.0025 | 5.3199 | N | 4.0889 | 8.9093 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.81 | N2 | 6.6274 | 0.60293 | N1 | 6.3768 | 0.80757 | N | 7.5343 | 49.6375 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.39 | 2.65 | N2 | 1.4224 | 1.6981 | N1 | 1.3916 | 2.6519 | N | 1.6726 | 13.7638 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.36 | 29 | N2 | 19.367 | 28.9817 | N1 | 19.3558 | 28.996 | N | 120.8199 | 2634.3818 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.34 | 138.05 | N2 | 48.4795 | 137.9797 | N1 | 48.3383 | 138.0461 | N | 118.9068 | 12243.8162 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.56 | 13.71 | N2 | 13.7411 | 2.3101 | N1 | 13.5612 | 13.707 | N | 18.9905 | 193.9454 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.55 | 3.11 | N2 | 4.5948 | 1.214 | N1 | 4.5515 | 3.1098 | N | 7.443 | 101.9641 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 10.99 | 15.95 | N2 | 11.6562 | 0.26736 | N1 | 10.995 | 15.9523 | N | 11.1757 | 24.8397 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.06 | 54.13 | N2 | 25.2447 | 1.4505 | N1 | 25.0643 | 54.1271 | N | 25.5977 | 86.9903 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 8.98 | 11.11 | N2 | 9.2733 | 1.2721 | N1 | 8.9797 | 11.1086 | N | 9.186 | 20.2661 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.02 | 2.48 | N2 | 6.0326 | 2.4786 | N1 | 6.0227 | 2.4791 | N | 13.3831 | 234.5589 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.63 | 3.68 | N2 | 3.8789 | 1.1289 | N1 | 3.6266 | 3.6778 | N | 3.7117 | 9.5227 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.31 | 10.68 | N2 | 10.0985 | 1.3046 | N1 | 9.3054 | 10.6783 | N | 9.3053 | 10.6783 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.25 | 0.76 | N2 | 1.3937 | 0.08981 | N1 | 1.2545 | 0.76112 | N | 1.2544 | 0.76112 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.69 | 2.26 | N2 | 14.7742 | 2.2576 | N1 | 14.6911 | 2.2586 | N | 20.5048 | 189.5306 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.89 | 5.24 | N2 | 12.966 | 5.2342 | N1 | 12.8928 | 5.2351 | N | 28.5741 | 496.9948 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.53 | 4.49 | N2 | 1.9845 | 0.25377 | N1 | 1.5738 | 4.4691 | N | 1.5332 | 4.4919 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.34 | 5.55 | N2 | 17.123 | 2.1307 | N1 | 16.3353 | 5.5509 | N | 22.5922 | 200.6351 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.9 | 7.96 | N2 | 6.3038 | 1.7684 | N1 | 5.9033 | 7.9606 | N | 6.0791 | 14.9784 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.43 | 1.17 | N2 | 2.4383 | 1.1647 | N1 | 2.43 | 1.1653 | N | 2.696 | 18.2122 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 0.96 | N2 | 3.4865 | 0.0625 | N1 | 3.2268 | 0.95963 | N | 3.2511 | 5.5807 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25failrate110
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.006127
failures_per_annum_per_100km_oh_line | 0.3191
failures_per_annum_per_100km_ug_cable | 0.0654
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.42 | 13.38 | N2 | 10.4517 | 0.78842 | N1 | 10.424 | 13.3799 | N | 11.5333 | 55.017 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.76 | 7.28 | N2 | 9.7796 | 7.276 | N1 | 9.7642 | 7.279 | N | 12.9846 | 674.7588 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.75 | 1.41 | N2 | 5.0067 | 0.46277 | N1 | 4.7482 | 1.4109 | N | 5.8599 | 43.0392 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.7 | 12.49 | N2 | 3.3571 | 1.1368 | N1 | 2.7201 | 3.0852 | N | 2.6997 | 12.4851 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 28.69 | 0.3 | N2 | 32.6736 | 0.60787 | N1 | 28.6865 | 0.2995 | N | 56.3126 | 365.258 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.29 | 2.31 | N2 | 7.3446 | 2.306 | N1 | 7.2946 | 2.3065 | N | 13.7721 | 217.2598 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.38 | 3.77 | N2 | 3.4299 | 0.83569 | N1 | 3.3786 | 3.7708 | N | 5.2457 | 67.6962 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.79 | 8.31 | N2 | 1.8859 | 3.3159 | N1 | 1.7872 | 8.3093 | N | 1.8039 | 25.6265 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.67 | 15.58 | N2 | 2.807 | 6.2173 | N1 | 2.6748 | 15.58 | N | 2.7434 | 48.0496 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.96 | N2 | 2.2568 | 0.95457 | N1 | 2.2322 | 0.95509 | N | 4.9658 | 77.6565 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.44 | 4.38 | N2 | 14.7569 | 1.3815 | N1 | 12.4416 | 4.3817 | N | 15.0918 | 141.8169 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.72 | 1.31 | N2 | 10.1822 | 2.6496 | N1 | 8.7193 | 1.3105 | N | 11.254 | 125.8065 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.69 | 5.46 | N2 | 31.0191 | 4.5238 | N1 | 30.6872 | 5.4638 | N | 43.4788 | 389.4366 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.28 | 1.55 | N2 | 3.8709 | 0.7537 | N1 | 3.2818 | 1.5523 | N | 4.4592 | 51.8117 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.62 | N2 | 8.1696 | 1.2725 | N1 | 7.8539 | 1.6174 | N | 8.1745 | 19.7333 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.05 | 2.34 | N2 | 2.1459 | 1.1467 | N1 | 2.0505 | 2.3446 | N | 2.2075 | 9.0519 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.86 | 2.82 | N2 | 2.8907 | 1.4462 | N1 | 2.8636 | 2.816 | N | 3.3448 | 22.2461 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.16 | 2.06 | N2 | 3.3672 | 0.28535 | N1 | 3.1585 | 2.058 | N | 3.1585 | 2.058 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.84 | 4.12 | N2 | 4.9601 | 1.282 | N1 | 4.8394 | 4.1237 | N | 7.8685 | 103.8427 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.58 | 4.59 | N2 | 4.9629 | 0.85086 | N1 | 4.5752 | 4.5913 | N | 4.6058 | 6.7877 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.31 | 20.45 | N2 | 32.3413 | 20.442 | N1 | 32.3083 | 20.4504 | N | 104.1817 | 1896.577 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.65 | N2 | 3.1918 | 1.5423 | N1 | 2.7616 | 0.64581 | N | 4.619 | 65.101 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.66 | 1.59 | N2 | 5.6968 | 1.5844 | N1 | 5.6551 | 1.5852 | N | 9.5217 | 128.8702 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.65 | 0.92 | N2 | 0.77629 | 1.1031 | N1 | 0.64959 | 0.91632 | N | 0.67469 | 4.6541 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.17 | 3.3 | N2 | 3.2159 | 0.68007 | N1 | 3.1676 | 3.3007 | N | 4.722 | 55.0874 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.13 | 1.75 | N2 | 3.1605 | 0.4291 | N1 | 3.1267 | 1.7463 | N | 3.9583 | 34.8971 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.42 | 5.25 | N2 | 4.4772 | 1.0487 | N1 | 4.4182 | 5.2517 | N | 6.8346 | 85.2964 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.64 | 7.48 | N2 | 6.7764 | 3.3125 | N1 | 6.6426 | 7.4802 | N | 7.565 | 269.472 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.08 | 2.3 | N2 | 2.1828 | 1.3716 | N1 | 2.0814 | 2.3032 | N | 2.2803 | 11.4307 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.07 | 7.39 | N2 | 8.1857 | 1.4207 | N1 | 8.066 | 7.394 | N | 11.4248 | 115.5812 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.88 | 4.26 | N2 | 3.9348 | 0.77107 | N1 | 3.8804 | 4.2639 | N | 5.6778 | 62.7146 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.5 | 2.37 | N2 | 1.8174 | 0.27146 | N1 | 1.4984 | 2.3691 | N | 1.651 | 11.8963 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 32.79 | 0.24 | N2 | 37.334 | 0.34986 | N1 | 32.7911 | 0.23776 | N | 60.0302 | 368.8309 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.6 | 1.37 | N2 | 1.898 | 0.29475 | N1 | 1.602 | 1.3653 | N | 1.9189 | 17.0316 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 66.59 | 63.04 | N2 | 75.7066 | 1.2053 | N1 | 66.5901 | 63.0377 | N | 66.824 | 74.4654 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.58 | 0.91 | N2 | 1.8325 | 1.2329 | N1 | 1.577 | 0.9077 | N | 1.7788 | 14.5233 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.4 | 5 | N2 | 4.4251 | 0.67587 | N1 | 4.397 | 5.0038 | N | 6.1338 | 57.178 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.18 | 6.85 | N2 | 5.4936 | 1.9214 | N1 | 5.1818 | 6.8503 | N | 5.3619 | 15.9492 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.75 | 1.72 | N2 | 5.087 | 1.2192 | N1 | 4.7487 | 1.7237 | N | 4.8709 | 11.5995 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.36 | 6.97 | N2 | 6.4745 | 0.3796 | N1 | 6.3619 | 6.9711 | N | 6.806 | 26.2203 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.97 | 0.32 | N2 | 4.9787 | 0.31937 | N1 | 4.9667 | 0.31969 | N | 5.8178 | 28.2184 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.28 | 2.73 | N2 | 10.3414 | 2.7264 | N1 | 10.2754 | 2.727 | N | 18.2816 | 256.87 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.3 | 6.16 | N2 | 8.3228 | 0.99244 | N1 | 8.3012 | 6.1626 | N | 9.3119 | 50.6758 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.82 | 1.07 | N2 | 4.8201 | 1.0749 | N1 | 5.0305 | 4.0417 | N | 7.4487 | 87.5038 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.14 | 0.65 | N2 | 4.8201 | 1.0749 | N1 | 4.1367 | 0.65035 | N | 6.1361 | 69.9448 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.8 | 1.86 | N2 | 1.8238 | 0.32968 | N1 | 1.7982 | 1.8631 | N | 2.4834 | 26.7068 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.13 | 0.77 | N2 | 2.1386 | 0.76561 | N1 | 2.1265 | 0.76603 | N | 3.9161 | 62.0265 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.13 | 10.2 | N2 | 13.8619 | 1.0664 | N1 | 13.1253 | 10.1959 | N | 15.381 | 87.08 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.35 | 1.35 | N2 | 1.4259 | 0.65366 | N1 | 1.3479 | 1.3498 | N | 1.4003 | 5.3759 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.92 | N2 | 4.0777 | 0.92148 | N1 | 4.0442 | 0.92197 | N | 6.3038 | 74.9515 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.36 | 1.95 | N2 | 1.6289 | 0.87221 | N1 | 1.3561 | 1.9473 | N | 1.5691 | 12.5034 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.83 | 6.45 | N2 | 6.0991 | 0.48966 | N1 | 5.8306 | 6.446 | N | 6.8469 | 39.4831 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.82 | 2.45 | N2 | 3.2751 | 0.47157 | N1 | 2.8208 | 2.4546 | N | 3.5336 | 38.1831 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-2 | 10.15 | 1.58 | N2 | 10.1546 | 1.5793 | N1 | 10.1619 | 3.9088 | N | 13.5064 | 130.4805 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.52 | 10.97 | N2 | 10.6517 | 1.6334 | N1 | 10.5168 | 10.9718 | N | 14.0749 | 132.7836 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.61 | 1.4 | N2 | 0.78341 | 0.11795 | N1 | 0.61655 | 1.1612 | N | 0.60534 | 1.3994 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.05 | 1.77 | N2 | 1.2445 | 0.84258 | N1 | 1.0513 | 1.7749 | N | 1.0708 | 7.562 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.85 | 6.06 | N2 | 4.9063 | 1.212 | N1 | 4.8507 | 6.056 | N | 7.667 | 98.5843 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.85 | 4.5 | N2 | 15.9489 | 4.4973 | N1 | 15.8522 | 4.4982 | N | 31.0043 | 423.7132 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.5 | 2.75 | N2 | 1.5606 | 1.4805 | N1 | 1.4978 | 2.75 | N | 1.7367 | 11.9663 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.06 | N2 | 6.3826 | 0.83662 | N1 | 6.1439 | 1.055 | N | 8.3214 | 76.2528 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.67 | 2.99 | N2 | 32.7895 | 1.1036 | N1 | 31.6675 | 2.9947 | N | 34.2404 | 101.8595 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.08 | 8.55 | N2 | 12.1001 | 8.5472 | N1 | 12.0803 | 8.5489 | N | 38.2975 | 810.145 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.55 | 0.91 | N2 | 7.784 | 0.52272 | N1 | 7.5452 | 0.91436 | N | 8.5804 | 43.5065 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.63 | 2.16 | N2 | 6.6724 | 2.1567 | N1 | 6.6259 | 2.1572 | N | 12.8903 | 203.1926 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.78 | N2 | 4.497 | 3.7765 | N1 | 4.4843 | 3.7801 | N | 5.6598 | 264.8743 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.27 | 9.13 | N2 | 4.4808 | 1.6348 | N1 | 4.2733 | 9.1281 | N | 4.3908 | 13.7302 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.99 | 7.05 | N2 | 7.1017 | 0.6799 | N1 | 6.9909 | 7.0455 | N | 8.1028 | 47.0396 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.14 | 1.33 | N2 | 7.0494 | 2.0105 | N1 | 6.138 | 1.3267 | N | 9.2159 | 131.4029 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.64 | 2.08 | N2 | 1.6858 | 1.2049 | N1 | 1.6418 | 2.0818 | N | 2.0647 | 18.7483 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 17.02 | 21.74 | N2 | 17.3751 | 1.6299 | N1 | 17.0208 | 21.7425 | N | 18.6802 | 90.4144 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 27.72 | 0.22 | N2 | 27.7198 | 0.21966 | N1 | 27.7197 | 0.21968 | N | 45.8876 | 234.0946 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.75 | 2.92 | N2 | 2.0527 | 0.78922 | N1 | 1.7477 | 2.919 | N | 1.9276 | 11.7247 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.63 | 4.72 | N2 | 4.8758 | 0.68494 | N1 | 4.6298 | 4.7156 | N | 4.6298 | 4.7156 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.77 | 3.56 | N2 | 10.7743 | 3.5552 | N1 | 10.7717 | 3.556 | N | 20.998 | 308.1507 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.92 | 0.99 | N2 | 14.9184 | 0.99022 | N1 | 14.9178 | 0.99037 | N | 19.3173 | 56.5441 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.27 | 0.99 | N2 | 17.3046 | 0.98606 | N1 | 17.2691 | 0.98624 | N | 21.1892 | 50.5136 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.31 | 8.35 | N2 | 24.328 | 1.2719 | N1 | 24.311 | 8.3487 | N | 26.4885 | 84.2067 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.47 | 2.68 | N2 | 9.5301 | 2.6777 | N1 | 9.4685 | 2.6783 | N | 17.4561 | 252.2825 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.05 | 6.52 | N2 | 4.315 | 1.3304 | N1 | 4.0502 | 6.5181 | N | 4.1646 | 10.9097 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.39 | 1.03 | N2 | 6.6442 | 0.76882 | N1 | 6.3916 | 1.0274 | N | 7.9294 | 60.752 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.41 | 1.39 | N2 | 1.4414 | 1.0592 | N1 | 1.4136 | 1.39 | N | 1.7814 | 16.8317 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.65 | 36.06 | N2 | 19.6653 | 36.0358 | N1 | 19.6486 | 36.0571 | N | 144.1793 | 3225.3088 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.6 | 172.69 | N2 | 48.7491 | 172.5959 | N1 | 48.5952 | 172.695 | N | 135.5733 | 14990.83 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.69 | 16.78 | N2 | 13.7906 | 2.9171 | N1 | 13.6908 | 16.782 | N | 20.5473 | 237.1875 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.58 | 1.53 | N2 | 4.6174 | 1.5328 | N1 | 4.5812 | 1.5337 | N | 8.2229 | 124.6912 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.04 | 0.95 | N2 | 11.6691 | 0.33578 | N1 | 11.042 | 0.94859 | N | 11.3831 | 30.4292 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.27 | 1.93 | N2 | 25.3103 | 1.9272 | N1 | 25.2716 | 1.9286 | N | 26.3344 | 106.4246 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.07 | 13.61 | N2 | 9.2943 | 0.33412 | N1 | 9.0744 | 13.6099 | N | 9.3523 | 24.8237 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.05 | 3.04 | N2 | 6.066 | 3.0406 | N1 | 6.0514 | 3.0412 | N | 15.2135 | 286.834 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.66 | 4.5 | N2 | 3.8974 | 1.3907 | N1 | 3.6609 | 4.5004 | N | 3.7916 | 11.6546 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.39 | 13.08 | N2 | 10.1188 | 1.606 | N1 | 9.3951 | 13.0769 | N | 9.395 | 13.0769 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.93 | N2 | 1.4028 | 0.1124 | N1 | 1.2649 | 0.93287 | N | 1.2649 | 0.93287 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.74 | 2.46 | N2 | 14.8279 | 2.8508 | N1 | 14.7371 | 2.4607 | N | 22.1965 | 231.7886 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.95 | 6.45 | N2 | 13.0342 | 6.4509 | N1 | 12.9541 | 6.4523 | N | 32.4421 | 607.7723 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.57 | 5.49 | N2 | 1.9955 | 0.31376 | N1 | 1.6143 | 5.4619 | N | 1.5739 | 5.4897 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.39 | 6.82 | N2 | 17.1547 | 2.6523 | N1 | 16.3948 | 6.8163 | N | 24.2854 | 245.7238 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.97 | 1.34 | N2 | 6.3225 | 1.1212 | N1 | 5.9682 | 1.3405 | N | 6.2065 | 18.3578 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.43 | N2 | 2.4565 | 1.4314 | N1 | 2.4442 | 1.4323 | N | 2.8338 | 22.2715 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.24 | 1.19 | N2 | 3.4963 | 0.09335 | N1 | 3.2389 | 1.1856 | N | 3.297 | 6.8432 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25lives70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 28
oh_line_life_in_yrs | 35
ug_cable_life_in_yrs | 31.5
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 11.09 | 12.14 | N2 | 11.1936 | 0.69847 | N1 | 11.0931 | 12.1426 | N | 12.036 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 10.46 | 6.59 | N2 | 10.4711 | 6.5904 | N1 | 10.4584 | 6.593 | N | 13.2502 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 5.09 | 1.26 | N2 | 5.3845 | 0.41721 | N1 | 5.0859 | 1.2629 | N | 6.0405 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.82 | 11.35 | N2 | 3.5779 | 1.0303 | N1 | 2.8894 | 2.8048 | N | 2.8156 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 31.16 | 5.64 | N2 | 35.4953 | 0.5367 | N1 | 31.1567 | 5.638 | N | 55.3849 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.8 | 10.67 | N2 | 7.8876 | 2.3893 | N1 | 7.7982 | 10.6702 | N | 13.5643 | 197.4535 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.6 | 3.43 | N2 | 3.6658 | 0.74876 | N1 | 3.5979 | 3.4257 | N | 5.2463 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.91 | 7.55 | N2 | 2.0209 | 2.9978 | N1 | 1.9071 | 7.5519 | N | 1.9079 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.85 | 14.16 | N2 | 3.0098 | 5.6209 | N1 | 2.8529 | 14.1599 | N | 2.8944 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.39 | 0.85 | N2 | 2.4185 | 0.85392 | N1 | 2.3862 | 0.85434 | N | 4.8226 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 13.3 | 3.98 | N2 | 15.84 | 1.6117 | N1 | 13.303 | 3.9777 | N | 15.3727 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 9.33 | 1.19 | N2 | 10.8724 | 2.4 | N1 | 9.3322 | 1.1914 | N | 11.3421 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 32.91 | 4.94 | N2 | 33.3218 | 4.0565 | N1 | 32.9143 | 4.9378 | N | 44.2752 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.5 | 1.41 | N2 | 4.1387 | 0.6753 | N1 | 3.5036 | 1.4112 | N | 4.4767 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 8.42 | 1.45 | N2 | 8.7772 | 1.143 | N1 | 8.4199 | 1.4543 | N | 8.6553 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.18 | 3.35 | N2 | 2.2871 | 1.0409 | N1 | 2.178 | 3.3518 | N | 2.3067 | 8.2264 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 3.06 | 2.56 | N2 | 3.0963 | 1.3065 | N1 | 3.0556 | 2.5577 | N | 3.4622 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.38 | 1.87 | N2 | 3.6153 | 0.25637 | N1 | 3.3769 | 1.8693 | N | 3.3769 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 5.16 | 3.75 | N2 | 5.3029 | 1.1486 | N1 | 5.1613 | 3.7453 | N | 7.8493 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.88 | 4.17 | N2 | 5.3328 | 0.76504 | N1 | 4.8835 | 4.1672 | N | 4.904 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 34.54 | 18.5 | N2 | 34.5682 | 18.4931 | N1 | 34.5409 | 18.5001 | N | 99.4562 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.96 | 0.59 | N2 | 3.4215 | 1.3797 | N1 | 2.9583 | 0.58712 | N | 4.5513 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 6.02 | 6.98 | N2 | 6.1181 | 1.4173 | N1 | 6.0241 | 6.985 | N | 9.4646 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.69 | 0.83 | N2 | 0.81957 | 1.0014 | N1 | 0.68746 | 0.83304 | N | 0.69329 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.37 | 3 | N2 | 3.4371 | 0.60933 | N1 | 3.3734 | 2.9986 | N | 4.74 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.34 | 1.59 | N2 | 3.3956 | 0.38384 | N1 | 3.3433 | 1.5862 | N | 4.0427 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.71 | 4.77 | N2 | 4.8091 | 0.93808 | N1 | 4.71 | 4.771 | N | 6.8467 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 7.12 | 6.79 | N2 | 7.2866 | 2.9632 | N1 | 7.1202 | 6.7941 | N | 7.8499 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.22 | 3.5 | N2 | 2.3361 | 1.2452 | N1 | 2.2173 | 3.504 | N | 2.3799 | 10.3845 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.61 | 6.72 | N2 | 8.7711 | 1.2726 | N1 | 8.612 | 6.7152 | N | 11.5646 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 4.14 | 3.87 | N2 | 4.2267 | 0.68975 | N1 | 4.1372 | 3.8736 | N | 5.717 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.59 | 2.15 | N2 | 1.9408 | 0.24519 | N1 | 1.5894 | 2.1538 | N | 1.7019 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 35.64 | 0.22 | N2 | 40.5645 | 0.30895 | N1 | 35.637 | 0.21612 | N | 59.3725 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.7 | 2.06 | N2 | 2.0266 | 0.26409 | N1 | 1.7032 | 2.0573 | N | 1.9464 | 15.4837 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 71.87 | 57.28 | N2 | 82.3862 | 1.0828 | N1 | 71.8669 | 57.2802 | N | 72.0352 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.68 | 1.65 | N2 | 1.9505 | 1.1177 | N1 | 1.6802 | 1.6504 | N | 1.8119 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.71 | 4.55 | N2 | 4.7801 | 0.60246 | N1 | 4.7077 | 4.5481 | N | 6.2364 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.51 | 8.66 | N2 | 5.8979 | 1.7351 | N1 | 5.5149 | 8.6578 | N | 5.6636 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 5.09 | 1.56 | N2 | 5.4639 | 1.1034 | N1 | 5.085 | 1.5584 | N | 5.1597 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.79 | 6.33 | N2 | 6.9567 | 1.547 | N1 | 6.7877 | 6.3276 | N | 7.153 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 5.32 | 0.49 | N2 | 5.3309 | 0.49017 | N1 | 5.321 | 0.49095 | N | 6.0489 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 11.01 | 2.83 | N2 | 11.1092 | 2.8252 | N1 | 11.0082 | 2.8266 | N | 18.0988 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.92 | 7.62 | N2 | 8.9687 | 3.1538 | N1 | 8.9239 | 7.6165 | N | 9.7356 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 5.2 | 0.96 | N2 | 5.2045 | 0.95816 | N1 | 5.4136 | 7.4825 | N | 7.4785 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.45 | 0.59 | N2 | 5.2045 | 0.95816 | N1 | 4.4512 | 0.59124 | N | 6.174 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.91 | 1.69 | N2 | 1.947 | 0.29539 | N1 | 1.9137 | 1.6928 | N | 2.5054 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.27 | 0.69 | N2 | 2.282 | 0.68598 | N1 | 2.2719 | 0.68633 | N | 3.8511 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 14.03 | 9.26 | N2 | 14.8965 | 0.40216 | N1 | 14.0257 | 9.2616 | N | 15.9766 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.43 | 2.17 | N2 | 1.5253 | 0.59335 | N1 | 1.4345 | 2.1674 | N | 1.471 | 4.884 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.33 | 0.82 | N2 | 4.3795 | 0.8243 | N1 | 4.3319 | 0.8247 | N | 6.306 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.44 | 1.77 | N2 | 1.7311 | 1.5594 | N1 | 1.4376 | 1.7704 | N | 1.5998 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 6.22 | 5.85 | N2 | 6.5595 | 0.43613 | N1 | 6.2159 | 5.851 | N | 7.0978 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 3.01 | 2.23 | N2 | 3.502 | 0.42251 | N1 | 3.0052 | 2.2316 | N | 3.5692 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.81 | 14.48 | N2 | 10.9148 | 1.4126 | N1 | 10.8146 | 14.4819 | N | 13.7309 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 11.22 | 9.96 | N2 | 11.4493 | 1.461 | N1 | 11.2211 | 9.9648 | N | 14.3286 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.64 | 1.27 | N2 | 0.83628 | 0.10523 | N1 | 0.6506 | 1.0556 | N | 0.63703 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-0 | 1.11 | 6.87 | N2 | 1.3238 | 0.76487 | N1 | 1.1147 | 1.6136 | N | 1.1079 | 6.8747 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 5.17 | 5.5 | N2 | 5.27 | 1.0842 | N1 | 5.1697 | 5.5017 | N | 7.6652 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 16.98 | 4.07 | N2 | 17.1263 | 4.0714 | N1 | 16.9762 | 4.0722 | N | 30.4708 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.59 | 2.5 | N2 | 1.6656 | 1.3437 | N1 | 1.5894 | 2.4993 | N | 1.7946 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.58 | 1.16 | N2 | 6.8624 | 0.75361 | N1 | 6.5848 | 1.1622 | N | 8.477 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 33.98 | 2.71 | N2 | 35.2707 | 0.99624 | N1 | 33.9795 | 2.7119 | N | 36.0952 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.91 | 7.74 | N2 | 12.9304 | 7.7353 | N1 | 12.914 | 7.7367 | N | 36.5247 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 8.09 | 1.06 | N2 | 8.3674 | 0.46723 | N1 | 8.0926 | 1.0615 | N | 8.9627 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 7.1 | 2.24 | N2 | 7.1648 | 2.2345 | N1 | 7.0955 | 2.2356 | N | 12.6649 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.8 | 3.35 | N2 | 4.8115 | 3.3477 | N1 | 4.801 | 3.3507 | N | 5.8031 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.53 | 8.29 | N2 | 4.8089 | 1.4824 | N1 | 4.5334 | 8.2898 | N | 4.6335 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 7.46 | 6.39 | N2 | 7.6319 | 0.60106 | N1 | 7.4627 | 6.3925 | N | 8.4253 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.57 | 7.18 | N2 | 7.572 | 1.7985 | N1 | 6.5739 | 7.1819 | N | 9.1788 | 119.458 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.75 | 1.89 | N2 | 1.7943 | 1.0924 | N1 | 1.7452 | 1.8918 | N | 2.1061 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 18.13 | 19.75 | N2 | 18.6839 | 1.4226 | N1 | 18.133 | 19.7476 | N | 19.5039 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 30.12 | 0.19 | N2 | 30.1193 | 0.19398 | N1 | 30.1191 | 0.19399 | N | 46.1413 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.85 | 2.65 | N2 | 2.1886 | 0.71637 | N1 | 1.8481 | 2.6538 | N | 1.9769 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.94 | 4.28 | N2 | 5.2183 | 0.61406 | N1 | 4.9355 | 4.2811 | N | 4.9354 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 11.59 | 3.19 | N2 | 11.5965 | 3.1938 | N1 | 11.5943 | 3.1945 | N | 20.7258 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 16.15 | 0.86 | N2 | 16.1465 | 0.85741 | N1 | 16.1459 | 0.85754 | N | 20.0311 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 18.67 | 0.85 | N2 | 18.7357 | 0.85006 | N1 | 18.6725 | 0.85021 | N | 22.1581 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 26.15 | 7.56 | N2 | 26.2473 | 1.1185 | N1 | 26.1546 | 7.5573 | N | 28.0115 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 10.14 | 2.42 | N2 | 10.2366 | 2.4242 | N1 | 10.1426 | 2.4246 | N | 17.2298 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.31 | 5.92 | N2 | 4.6322 | 1.202 | N1 | 4.3078 | 5.9183 | N | 4.4053 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.85 | 0.92 | N2 | 7.1449 | 0.68442 | N1 | 6.8525 | 0.91564 | N | 8.1603 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.5 | 2.95 | N2 | 1.5367 | 1.8897 | N1 | 1.4991 | 2.9473 | N | 1.8151 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 20.89 | 32.5 | N2 | 20.903 | 32.4807 | N1 | 20.8891 | 32.4984 | N | 133.7297 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 51.98 | 155.19 | N2 | 52.2193 | 155.1076 | N1 | 51.98 | 155.1895 | N | 130.5583 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 14.59 | 15.24 | N2 | 14.8172 | 2.6094 | N1 | 14.5927 | 15.2431 | N | 20.6644 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.89 | 3.46 | N2 | 4.9571 | 1.3712 | N1 | 4.8949 | 3.4583 | N | 8.1266 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.83 | 17.75 | N2 | 12.5603 | 0.30116 | N1 | 11.8336 | 17.7462 | N | 12.0399 | 27.6312 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 27.02 | 60.18 | N2 | 27.1384 | 1.6818 | N1 | 27.0168 | 60.1784 | N | 27.6342 | 96.7024 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.66 | 12.36 | N2 | 9.9868 | 1.4217 | N1 | 9.6628 | 12.3577 | N | 9.8967 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.47 | 2.76 | N2 | 6.4783 | 2.7591 | N1 | 6.4661 | 2.7596 | N | 14.6744 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.9 | 4.09 | N2 | 4.1823 | 1.2593 | N1 | 3.9008 | 4.0889 | N | 4.0001 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 10.01 | 11.88 | N2 | 10.8816 | 1.4548 | N1 | 10.0108 | 11.8764 | N | 10.0107 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.35 | 0.85 | N2 | 1.5034 | 0.10098 | N1 | 1.3492 | 0.84687 | N | 1.3491 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 15.79 | 2.55 | N2 | 15.9313 | 2.55 | N1 | 15.7904 | 2.5513 | N | 22.3141 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 13.86 | 5.84 | N2 | 13.9843 | 5.8401 | N1 | 13.8606 | 5.8412 | N | 31.3445 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.65 | 4.99 | N2 | 2.1315 | 0.2836 | N1 | 1.6953 | 4.9655 | N | 1.6518 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 17.56 | 6.18 | N2 | 18.4525 | 2.3893 | N1 | 17.5565 | 6.1822 | N | 24.5555 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 6.35 | 8.86 | N2 | 6.7948 | 1.8627 | N1 | 6.353 | 8.8597 | N | 6.5515 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.61 | 1.3 | N2 | 2.6196 | 1.2977 | N1 | 2.6094 | 1.2984 | N | 2.9161 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.47 | 1.07 | N2 | 3.7477 | 0.07716 | N1 | 3.4673 | 1.072 | N | 3.4993 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25lives130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 52
oh_line_life_in_yrs | 65
ug_cable_life_in_yrs | 58.5
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.09 | 12.14 | N2 | 10.1474 | 0.69847 | N1 | 10.0941 | 12.1426 | N | 11.0769 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.48 | 6.59 | N2 | 9.494 | 6.5904 | N1 | 9.4814 | 6.593 | N | 12.3558 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.6 | 1.26 | N2 | 4.8475 | 0.41721 | N1 | 4.6049 | 1.2629 | N | 5.5937 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.59 | 11.35 | N2 | 3.2375 | 1.0303 | N1 | 2.6303 | 2.8048 | N | 2.5907 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 27.65 | 0.27 | N2 | 31.4952 | 0.5367 | N1 | 27.6531 | 0.27224 | N | 52.4908 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.07 | 2.09 | N2 | 7.1062 | 2.0877 | N1 | 7.0736 | 2.088 | N | 12.9079 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.27 | 3.43 | N2 | 3.3267 | 0.74876 | N1 | 3.2727 | 3.4257 | N | 4.951 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.73 | 7.55 | N2 | 1.8229 | 2.9978 | N1 | 1.7302 | 7.5519 | N | 1.7398 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.59 | 14.16 | N2 | 2.7142 | 5.6209 | N1 | 2.589 | 14.1599 | N | 2.6433 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.16 | 0.85 | N2 | 2.1798 | 0.85392 | N1 | 2.1626 | 0.85434 | N | 4.6289 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.06 | 3.98 | N2 | 14.2821 | 1.6117 | N1 | 12.0627 | 3.9777 | N | 14.3414 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.46 | 1.19 | N2 | 9.8703 | 2.4 | N1 | 8.4641 | 1.1914 | N | 10.6559 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 29.77 | 4.94 | N2 | 30.0643 | 4.0565 | N1 | 29.7726 | 4.9378 | N | 41.2873 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.18 | 1.41 | N2 | 3.7551 | 0.6753 | N1 | 3.1824 | 1.4112 | N | 4.2156 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.62 | 1.45 | N2 | 7.9158 | 1.143 | N1 | 7.6199 | 1.4543 | N | 7.8895 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 1.99 | 2.13 | N2 | 2.0788 | 1.0409 | N1 | 1.985 | 2.1305 | N | 2.1214 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.77 | 2.56 | N2 | 2.7957 | 1.3065 | N1 | 2.7723 | 2.5577 | N | 3.1977 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.06 | 1.87 | N2 | 3.2607 | 0.25637 | N1 | 3.06 | 1.8693 | N | 3.0599 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.69 | 3.75 | N2 | 4.8116 | 1.1486 | N1 | 4.6907 | 3.7453 | N | 7.4188 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.43 | 4.17 | N2 | 4.8044 | 0.76504 | N1 | 4.4301 | 4.1672 | N | 4.4551 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 31.3 | 18.5 | N2 | 31.3252 | 18.4931 | N1 | 31.2979 | 18.5001 | N | 96.4477 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.68 | 0.59 | N2 | 3.0842 | 1.3797 | N1 | 2.6778 | 0.58712 | N | 4.3296 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.47 | 6.98 | N2 | 5.5108 | 1.4173 | N1 | 5.4714 | 6.985 | N | 8.9567 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.63 | 0.83 | N2 | 0.74865 | 1.0014 | N1 | 0.62761 | 0.83304 | N | 0.64393 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.07 | 3 | N2 | 3.1191 | 0.60933 | N1 | 3.0684 | 2.9986 | N | 4.4635 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.03 | 1.59 | N2 | 3.057 | 0.38384 | N1 | 3.0298 | 1.5862 | N | 3.7639 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.28 | 4.77 | N2 | 4.3309 | 0.93808 | N1 | 4.2755 | 4.771 | N | 6.4489 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.44 | 6.79 | N2 | 6.5593 | 2.9632 | N1 | 6.4427 | 6.7941 | N | 7.2394 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.01 | 2.09 | N2 | 2.1094 | 1.2452 | N1 | 2.0143 | 2.0923 | N | 2.1877 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 7.81 | 6.72 | N2 | 7.9365 | 1.2726 | N1 | 7.809 | 6.7152 | N | 10.8233 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.76 | 3.87 | N2 | 3.8061 | 0.68975 | N1 | 3.7554 | 3.8736 | N | 5.3683 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.45 | 2.15 | N2 | 1.7619 | 0.24519 | N1 | 1.4491 | 2.1538 | N | 1.5778 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 31.61 | 0.22 | N2 | 35.9899 | 0.30895 | N1 | 31.6103 | 0.21612 | N | 56.0588 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.55 | 1.24 | N2 | 1.8399 | 0.26409 | N1 | 1.5514 | 1.2412 | N | 1.8217 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 64.08 | 57.28 | N2 | 72.919 | 1.0828 | N1 | 64.0817 | 57.2802 | N | 64.2833 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.53 | 0.83 | N2 | 1.7741 | 1.1177 | N1 | 1.5286 | 0.82521 | N | 1.6916 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.24 | 4.55 | N2 | 4.2727 | 0.60246 | N1 | 4.2433 | 4.5481 | N | 5.8029 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.01 | 6.22 | N2 | 5.3163 | 1.7351 | N1 | 5.0119 | 6.2188 | N | 5.1693 | 14.485 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.61 | 1.56 | N2 | 4.9248 | 1.1034 | N1 | 4.6054 | 1.5584 | N | 4.7024 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.16 | 6.33 | N2 | 6.2715 | 0.33551 | N1 | 6.1582 | 6.3276 | N | 6.547 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.82 | 0.29 | N2 | 4.8333 | 0.2877 | N1 | 4.8234 | 0.28796 | N | 5.5782 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 9.96 | 2.47 | N2 | 10.0073 | 2.4682 | N1 | 9.9649 | 2.4687 | N | 17.1689 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.01 | 5.6 | N2 | 8.0523 | 0.8618 | N1 | 8.0069 | 5.5972 | N | 8.8972 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.65 | 0.96 | N2 | 4.6534 | 0.95816 | N1 | 4.8498 | 3.6496 | N | 7.0156 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.01 | 0.59 | N2 | 4.6534 | 0.95816 | N1 | 4.0057 | 0.59124 | N | 5.7798 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.74 | 1.69 | N2 | 1.7678 | 0.29539 | N1 | 1.7414 | 1.6928 | N | 2.3522 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.06 | 0.69 | N2 | 2.0725 | 0.68598 | N1 | 2.0625 | 0.68633 | N | 3.6711 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 12.72 | 9.26 | N2 | 13.4294 | 0.95152 | N1 | 12.7199 | 9.2616 | N | 14.7292 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.3 | 1.23 | N2 | 1.3774 | 0.59335 | N1 | 1.3046 | 1.2265 | N | 1.3473 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 3.92 | 0.82 | N2 | 3.9442 | 0.8243 | N1 | 3.9216 | 0.8247 | N | 5.9447 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.31 | 1.77 | N2 | 1.5769 | 1.5594 | N1 | 1.3111 | 1.7704 | N | 1.4928 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.64 | 5.85 | N2 | 5.9049 | 0.43613 | N1 | 5.6429 | 5.851 | N | 6.5504 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.73 | 2.23 | N2 | 3.1772 | 0.42251 | N1 | 2.7329 | 2.2316 | N | 3.3488 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-2 | 9.83 | 1.41 | N2 | 9.8284 | 1.4126 | N1 | 9.8297 | 14.4819 | N | 12.8197 | 118.5846 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.18 | 9.96 | N2 | 10.3097 | 1.461 | N1 | 10.18 | 9.9648 | N | 13.3654 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.58 | 1.27 | N2 | 0.75565 | 0.10523 | N1 | 0.59397 | 1.0556 | N | 0.58248 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.02 | 1.61 | N2 | 1.2043 | 0.76487 | N1 | 1.0165 | 1.6136 | N | 1.0249 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.69 | 5.5 | N2 | 4.7463 | 1.0842 | N1 | 4.6936 | 5.5017 | N | 7.2286 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.37 | 4.07 | N2 | 15.4321 | 4.0714 | N1 | 15.3704 | 4.0722 | N | 29.033 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.45 | 2.5 | N2 | 1.506 | 1.3437 | N1 | 1.4467 | 2.4993 | N | 1.6592 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 5.96 | 1.16 | N2 | 6.1789 | 0.75361 | N1 | 5.9594 | 1.1622 | N | 7.9049 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 30.73 | 2.71 | N2 | 31.7898 | 0.99624 | N1 | 30.7341 | 2.7119 | N | 32.9846 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 11.7 | 7.74 | N2 | 11.7186 | 7.7353 | N1 | 11.7023 | 7.7367 | N | 35.4457 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.32 | 1.06 | N2 | 7.5424 | 0.46723 | N1 | 7.3219 | 1.0615 | N | 8.2345 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.42 | 1.95 | N2 | 6.4553 | 1.9525 | N1 | 6.4249 | 1.9529 | N | 12.07 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.35 | 3.35 | N2 | 4.3638 | 3.3477 | N1 | 4.3533 | 3.3507 | N | 5.3963 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.13 | 8.29 | N2 | 4.3356 | 1.4824 | N1 | 4.1273 | 8.2898 | N | 4.2315 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.77 | 6.39 | N2 | 6.8785 | 0.60106 | N1 | 6.7686 | 6.3925 | N | 7.7605 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 5.95 | 1.21 | N2 | 6.8203 | 1.7985 | N1 | 5.9538 | 1.2061 | N | 8.6744 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.59 | 1.89 | N2 | 1.632 | 1.0924 | N1 | 1.5891 | 1.8918 | N | 1.9645 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.46 | 19.75 | N2 | 16.8204 | 1.4226 | N1 | 16.4638 | 19.7476 | N | 17.9193 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 26.72 | 0.19 | N2 | 26.7223 | 0.19398 | N1 | 26.7222 | 0.19399 | N | 43.0885 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.69 | 2.65 | N2 | 1.9888 | 0.71637 | N1 | 1.688 | 2.6538 | N | 1.8382 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.49 | 4.28 | N2 | 4.7322 | 0.61406 | N1 | 4.4866 | 4.2811 | N | 4.4866 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.41 | 3.19 | N2 | 10.4156 | 3.1938 | N1 | 10.4134 | 3.1945 | N | 19.6411 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.39 | 0.86 | N2 | 14.3921 | 0.85741 | N1 | 14.3916 | 0.85754 | N | 18.3644 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 16.67 | 0.85 | N2 | 16.6932 | 0.85006 | N1 | 16.6727 | 0.85021 | N | 20.1994 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 23.52 | 7.56 | N2 | 23.541 | 1.1185 | N1 | 23.524 | 7.5573 | N | 25.4564 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.18 | 2.42 | N2 | 9.2217 | 2.4242 | N1 | 9.182 | 2.4246 | N | 16.3744 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 3.92 | 5.92 | N2 | 4.1755 | 1.202 | N1 | 3.916 | 5.9183 | N | 4.0175 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.2 | 0.92 | N2 | 6.4325 | 0.68442 | N1 | 6.2005 | 0.91564 | N | 7.5636 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.37 | 2.95 | N2 | 1.3909 | 0.95993 | N1 | 1.3667 | 2.9473 | N | 1.6924 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 18.95 | 32.5 | N2 | 18.9642 | 32.4807 | N1 | 18.9503 | 32.4984 | N | 132.0026 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 47.09 | 155.19 | N2 | 47.1848 | 155.1076 | N1 | 47.087 | 155.1895 | N | 125.9263 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.25 | 15.24 | N2 | 13.3459 | 2.6094 | N1 | 13.2464 | 15.2431 | N | 19.4167 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.44 | 3.46 | N2 | 4.4656 | 1.3712 | N1 | 4.4383 | 3.4583 | N | 7.7175 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 10.72 | 0.85 | N2 | 11.3048 | 0.30116 | N1 | 10.7159 | 0.84904 | N | 10.9811 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 24.51 | 1.68 | N2 | 24.5461 | 1.6818 | N1 | 24.5141 | 1.683 | N | 25.3096 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 8.78 | 12.36 | N2 | 9.0058 | 1.4217 | N1 | 8.7776 | 12.3577 | N | 9.0229 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 5.87 | 2.76 | N2 | 5.8822 | 2.7591 | N1 | 5.8701 | 2.7596 | N | 14.1517 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.54 | 4.09 | N2 | 3.7708 | 1.2593 | N1 | 3.543 | 4.0889 | N | 3.6543 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.09 | 11.88 | N2 | 9.8007 | 1.4548 | N1 | 9.0913 | 11.8764 | N | 9.0912 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.22 | 0.85 | N2 | 1.3562 | 0.10098 | N1 | 1.2247 | 0.84687 | N | 1.2246 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.29 | 2.55 | N2 | 14.3496 | 2.55 | N1 | 14.2917 | 2.5513 | N | 20.9717 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.56 | 5.84 | N2 | 12.607 | 5.8401 | N1 | 12.5558 | 5.8412 | N | 30.1787 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.52 | 4.99 | N2 | 1.9348 | 0.2836 | N1 | 1.5547 | 4.9655 | N | 1.5153 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 15.9 | 6.18 | N2 | 16.6153 | 2.3893 | N1 | 15.898 | 6.1822 | N | 22.9997 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.78 | 8.86 | N2 | 6.1216 | 1.0064 | N1 | 5.7763 | 8.8597 | N | 5.9825 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.37 | 1.3 | N2 | 2.3803 | 1.2977 | N1 | 2.3701 | 1.2984 | N | 2.706 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.14 | 1.07 | N2 | 3.3884 | 0.71611 | N1 | 3.141 | 1.072 | N | 3.1858 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25ugcostmult5
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 5
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 11.48 | 0.27 | N2 | 12.7858 | 0.5367 | N1 | 11.4755 | 0.27224 | N | 39.5723 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 13.11 | 0.22 | N2 | 14.5935 | 0.30895 | N1 | 13.1091 | 0.21612 | N | 41.2863 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 23.87 | 2.08 | N2 | 26.3934 | 1.0828 | N1 | 23.8678 | 2.0848 | N | 25.1734 | 67.664 | 0 | 0.3 | 0 | 0 | 0 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 10.84 | 0.19 | N2 | 10.8366 | 0.19398 | N1 | 10.8364 | 0.19399 | N | 28.9782 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25ugcostmult25
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 25
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 10.37 | 12.14 | N2 | 10.4404 | 0.69847 | N1 | 10.3739 | 12.1426 | N | 11.3455 | 49.968 | 0 | 0 | 0 | 0 | 0.2 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 9.75 | 6.59 | N2 | 9.7677 | 6.5904 | N1 | 9.755 | 6.593 | N | 12.6063 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 4.74 | 1.26 | N2 | 5.0006 | 0.41721 | N1 | 4.7403 | 1.2629 | N | 5.7195 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 2.65 | 11.35 | N2 | 3.3343 | 1.0303 | N1 | 2.7031 | 2.8048 | N | 2.6539 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 45.57 | 5.64 | N2 | 52.5451 | 0.5367 | N1 | 45.5708 | 5.638 | N | 67.1054 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 7.28 | 2.09 | N2 | 7.3293 | 2.0877 | N1 | 7.2819 | 2.088 | N | 13.093 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 3.36 | 3.43 | N2 | 3.4216 | 0.74876 | N1 | 3.3638 | 3.4257 | N | 5.0337 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.78 | 7.55 | N2 | 1.8794 | 2.9978 | N1 | 1.7801 | 7.5519 | N | 1.7872 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 2.66 | 14.16 | N2 | 2.7985 | 5.6209 | N1 | 2.6634 | 14.1599 | N | 2.7141 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.23 | 0.85 | N2 | 2.248 | 0.85392 | N1 | 2.2256 | 0.85434 | N | 4.6835 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 12.41 | 3.98 | N2 | 14.7254 | 1.6117 | N1 | 12.4113 | 3.9777 | N | 14.6315 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 8.71 | 1.19 | N2 | 10.151 | 2.4 | N1 | 8.7072 | 1.1914 | N | 10.848 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 30.66 | 4.94 | N2 | 30.988 | 4.0565 | N1 | 30.6577 | 4.9378 | N | 42.1294 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 3.27 | 1.41 | N2 | 3.8626 | 0.6753 | N1 | 3.2723 | 1.4112 | N | 4.2887 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 7.85 | 1.45 | N2 | 8.1603 | 1.143 | N1 | 7.8451 | 1.4543 | N | 8.1051 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.04 | 2.13 | N2 | 2.1371 | 1.0409 | N1 | 2.0397 | 2.1305 | N | 2.1733 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.85 | 2.56 | N2 | 2.8812 | 1.3065 | N1 | 2.8521 | 2.5577 | N | 3.2723 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 3.15 | 1.87 | N2 | 3.3615 | 0.25637 | N1 | 3.1494 | 1.8693 | N | 3.1493 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 4.82 | 3.75 | N2 | 4.9492 | 1.1486 | N1 | 4.8225 | 3.7453 | N | 7.5394 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 4.56 | 4.17 | N2 | 4.9549 | 0.76504 | N1 | 4.5578 | 4.1672 | N | 4.5816 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 32.21 | 18.5 | N2 | 32.2394 | 18.4931 | N1 | 32.2121 | 18.5001 | N | 97.2966 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.76 | 0.59 | N2 | 3.1805 | 1.3797 | N1 | 2.7569 | 0.58712 | N | 4.3922 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 5.63 | 6.98 | N2 | 5.6841 | 1.4173 | N1 | 5.6272 | 6.985 | N | 9.0999 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.64 | 0.83 | N2 | 0.76851 | 1.0014 | N1 | 0.64437 | 0.83304 | N | 0.65775 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 3.15 | 3 | N2 | 3.2081 | 0.60933 | N1 | 3.1538 | 2.9986 | N | 4.5409 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.12 | 1.59 | N2 | 3.1537 | 0.38384 | N1 | 3.1181 | 1.5862 | N | 3.8425 | 31.7154 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 4.4 | 4.77 | N2 | 4.4674 | 0.93808 | N1 | 4.398 | 4.771 | N | 6.5611 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 6.63 | 6.79 | N2 | 6.7668 | 2.9632 | N1 | 6.6336 | 6.7941 | N | 7.4116 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.07 | 2.09 | N2 | 2.174 | 1.2452 | N1 | 2.0717 | 2.0923 | N | 2.2418 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 8.04 | 6.72 | N2 | 8.1718 | 1.2726 | N1 | 8.0354 | 6.7152 | N | 11.0325 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 3.86 | 3.87 | N2 | 3.9262 | 0.68975 | N1 | 3.863 | 3.8736 | N | 5.4666 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.49 | 2.15 | N2 | 1.812 | 0.24519 | N1 | 1.4884 | 2.1538 | N | 1.6125 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 52.15 | 6.83 | N2 | 60.063 | 0.30895 | N1 | 52.1485 | 6.8341 | N | 72.7736 | 335.5287 | 0 | 0 | 0 | 0 | 0.1 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.59 | 1.24 | N2 | 1.8922 | 0.26409 | N1 | 1.5943 | 1.2412 | N | 1.8566 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 107.73 | 57.28 | N2 | 125.0084 | 1.0828 | N1 | 107.7275 | 57.2802 | N | 107.919 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.57 | 0.83 | N2 | 1.8235 | 1.1177 | N1 | 1.5715 | 0.82521 | N | 1.7253 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 4.38 | 4.55 | N2 | 4.4197 | 0.60246 | N1 | 4.3766 | 4.5481 | N | 5.9274 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 5.16 | 8.66 | N2 | 5.482 | 1.7351 | N1 | 5.1564 | 8.6578 | N | 5.3086 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 4.74 | 1.56 | N2 | 5.0782 | 1.1034 | N1 | 4.7404 | 1.5584 | N | 4.8311 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 6.34 | 6.33 | N2 | 6.4671 | 0.33551 | N1 | 6.3357 | 6.3276 | N | 6.7179 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 4.96 | 0.29 | N2 | 4.9728 | 0.2877 | N1 | 4.9629 | 0.28796 | N | 5.71 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 10.26 | 2.47 | N2 | 10.3216 | 2.4682 | N1 | 10.2588 | 2.4687 | N | 17.4312 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 8.27 | 7.62 | N2 | 8.3154 | 0.8618 | N1 | 8.2737 | 7.6165 | N | 9.1387 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 4.81 | 0.96 | N2 | 4.813 | 0.95816 | N1 | 5.0144 | 3.6496 | N | 7.1485 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 4.13 | 0.59 | N2 | 4.813 | 0.95816 | N1 | 4.1328 | 0.59124 | N | 5.8935 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.79 | 1.69 | N2 | 1.818 | 0.29539 | N1 | 1.7896 | 1.6928 | N | 2.3951 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.12 | 0.69 | N2 | 2.1312 | 0.68598 | N1 | 2.1211 | 0.68633 | N | 3.7215 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 13.09 | 9.26 | N2 | 13.8526 | 0.95152 | N1 | 13.0871 | 9.2616 | N | 15.0801 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.34 | 1.23 | N2 | 1.4196 | 0.59335 | N1 | 1.3416 | 1.2265 | N | 1.3821 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 4.04 | 0.82 | N2 | 4.0685 | 0.8243 | N1 | 4.0372 | 0.8247 | N | 6.0466 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.35 | 1.77 | N2 | 1.6201 | 1.5594 | N1 | 1.3465 | 1.7704 | N | 1.5228 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 5.8 | 5.85 | N2 | 6.0916 | 0.43613 | N1 | 5.8043 | 5.851 | N | 6.7046 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.81 | 2.23 | N2 | 3.2682 | 0.42251 | N1 | 2.8092 | 2.2316 | N | 3.4105 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 10.11 | 14.48 | N2 | 10.1383 | 1.4126 | N1 | 10.1072 | 14.4819 | N | 13.0766 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 10.47 | 9.96 | N2 | 10.6348 | 1.461 | N1 | 10.4735 | 9.9648 | N | 13.6371 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.6 | 1.27 | N2 | 0.77865 | 0.10523 | N1 | 0.60995 | 1.0556 | N | 0.59788 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 1.04 | 1.61 | N2 | 1.2378 | 0.76487 | N1 | 1.044 | 1.6136 | N | 1.0481 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 4.83 | 5.5 | N2 | 4.8957 | 1.0842 | N1 | 4.8277 | 5.5017 | N | 7.3517 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 15.82 | 4.07 | N2 | 15.9153 | 4.0714 | N1 | 15.8227 | 4.0722 | N | 29.4386 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.49 | 2.5 | N2 | 1.5515 | 1.3437 | N1 | 1.4869 | 2.4993 | N | 1.6974 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 6.14 | 1.16 | N2 | 6.3738 | 0.75361 | N1 | 6.1355 | 1.1622 | N | 8.0661 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 31.65 | 2.71 | N2 | 32.7779 | 0.99624 | N1 | 31.6479 | 2.7119 | N | 33.8606 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 12.04 | 7.74 | N2 | 12.0602 | 7.7353 | N1 | 12.0439 | 7.7367 | N | 35.7503 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 7.54 | 1.06 | N2 | 7.7768 | 0.46723 | N1 | 7.5389 | 1.0615 | N | 8.4395 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 6.61 | 1.95 | N2 | 6.6579 | 1.9525 | N1 | 6.6139 | 1.9529 | N | 12.2377 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 4.48 | 3.35 | N2 | 4.4892 | 3.3477 | N1 | 4.4787 | 3.3507 | N | 5.5103 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 4.24 | 8.29 | N2 | 4.4704 | 1.4824 | N1 | 4.2417 | 8.2898 | N | 4.3448 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 6.96 | 6.39 | N2 | 7.0927 | 0.60106 | N1 | 6.9642 | 6.3925 | N | 7.9479 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 6.13 | 1.21 | N2 | 7.0348 | 1.7985 | N1 | 6.1305 | 1.2061 | N | 8.8169 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.63 | 1.89 | N2 | 1.6774 | 1.0924 | N1 | 1.6328 | 1.8918 | N | 2.0042 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 16.93 | 19.75 | N2 | 17.3519 | 1.4226 | N1 | 16.9346 | 19.7476 | N | 18.3664 | 82.1605 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 44.38 | 8.57 | N2 | 44.5956 | 0.19398 | N1 | 44.3823 | 8.5716 | N | 58.9862 | 212.9358 | 0 | 0 | 0 | 0 | 0.1 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.73 | 2.65 | N2 | 2.0447 | 0.71637 | N1 | 1.7328 | 2.6538 | N | 1.8771 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 4.61 | 4.28 | N2 | 4.8684 | 0.61406 | N1 | 4.6123 | 4.2811 | N | 4.6123 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 10.75 | 3.19 | N2 | 10.7546 | 3.1938 | N1 | 10.7524 | 3.1945 | N | 19.954 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 14.9 | 0.86 | N2 | 14.9028 | 0.85741 | N1 | 14.9023 | 0.85754 | N | 18.8485 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 17.25 | 0.85 | N2 | 17.2882 | 0.85006 | N1 | 17.2528 | 0.85021 | N | 20.7689 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 24.28 | 7.56 | N2 | 24.3181 | 1.1185 | N1 | 24.2764 | 7.5573 | N | 26.1876 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 9.45 | 2.42 | N2 | 9.5112 | 2.4242 | N1 | 9.4526 | 2.4246 | N | 16.6157 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 4.03 | 5.92 | N2 | 4.3056 | 1.202 | N1 | 4.0263 | 5.9183 | N | 4.1267 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 6.38 | 0.92 | N2 | 6.6356 | 0.68442 | N1 | 6.3841 | 0.91564 | N | 7.7317 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.4 | 2.95 | N2 | 1.4332 | 1.8897 | N1 | 1.4041 | 2.9473 | N | 1.7269 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 19.5 | 32.5 | N2 | 19.5149 | 32.4807 | N1 | 19.5011 | 32.4984 | N | 132.4893 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 48.47 | 155.19 | N2 | 48.6129 | 155.1076 | N1 | 48.4657 | 155.1895 | N | 127.2326 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 13.63 | 15.24 | N2 | 13.7655 | 2.6094 | N1 | 13.6259 | 15.2431 | N | 19.7686 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 4.57 | 3.46 | N2 | 4.6059 | 1.3712 | N1 | 4.567 | 3.4583 | N | 7.8329 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 11.03 | 0.85 | N2 | 11.6625 | 0.30116 | N1 | 11.0341 | 0.84904 | N | 11.2793 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 25.24 | 1.68 | N2 | 25.2769 | 1.6818 | N1 | 25.2449 | 1.683 | N | 25.9659 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 9.03 | 12.36 | N2 | 9.2845 | 1.4217 | N1 | 9.027 | 12.3577 | N | 9.2691 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 6.04 | 2.76 | N2 | 6.0492 | 2.7591 | N1 | 6.037 | 2.7596 | N | 14.2981 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 3.64 | 4.09 | N2 | 3.888 | 1.2593 | N1 | 3.6437 | 4.0889 | N | 3.7516 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 9.35 | 11.88 | N2 | 10.1085 | 1.4548 | N1 | 9.3502 | 11.8764 | N | 9.3501 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.26 | 0.85 | N2 | 1.3981 | 0.10098 | N1 | 1.2597 | 0.84687 | N | 1.2596 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 14.71 | 2.55 | N2 | 14.8007 | 2.55 | N1 | 14.7139 | 2.5513 | N | 21.3504 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 12.92 | 5.84 | N2 | 12.9998 | 5.8401 | N1 | 12.9234 | 5.8412 | N | 30.5075 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.55 | 4.99 | N2 | 1.9899 | 0.2836 | N1 | 1.594 | 4.9655 | N | 1.5535 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 16.37 | 6.18 | N2 | 17.1386 | 2.3893 | N1 | 16.365 | 6.1822 | N | 23.4379 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 5.94 | 8.86 | N2 | 6.3138 | 1.0064 | N1 | 5.9386 | 8.8597 | N | 6.1427 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 2.44 | 1.3 | N2 | 2.4473 | 1.2977 | N1 | 2.4371 | 1.2984 | N | 2.7649 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.23 | 1.07 | N2 | 3.4913 | 0.07716 | N1 | 3.2328 | 1.072 | N | 3.274 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25lcostcoef70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0173
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 7.35 | 0.7 | N2 | 7.3606 | 0.69847 | N1 | 7.3476 | 0.69908 | N | 8.5027 | 49.968 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 6.88 | 6.59 | N2 | 6.8959 | 6.5904 | N1 | 6.8832 | 6.593 | N | 9.9554 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 3.43 | 1.26 | N2 | 3.6056 | 0.41721 | N1 | 3.4286 | 1.2629 | N | 4.485 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-1 | 1.97 | 2.8 | N2 | 2.4145 | 1.0303 | N1 | 1.9738 | 2.8048 | N | 2.0197 | 11.3505 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 20.94 | 0.27 | N2 | 23.7196 | 0.5367 | N1 | 20.94 | 0.27224 | N | 47.1439 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 5.28 | 2.09 | N2 | 5.3226 | 2.0877 | N1 | 5.2841 | 2.088 | N | 11.3172 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 2.42 | 3.43 | N2 | 2.4388 | 0.74876 | N1 | 2.4247 | 3.4257 | N | 4.1601 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.3 | 7.55 | N2 | 1.365 | 2.9978 | N1 | 1.3022 | 7.5519 | N | 1.3321 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 1.95 | 14.16 | N2 | 2.0295 | 5.6209 | N1 | 1.9488 | 14.1599 | N | 2.0336 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 1.63 | 0.85 | N2 | 1.6548 | 0.85392 | N1 | 1.6349 | 0.85434 | N | 4.1585 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 8.95 | 3.98 | N2 | 10.5441 | 1.6117 | N1 | 8.952 | 3.9777 | N | 11.7489 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 6.17 | 1.19 | N2 | 7.2166 | 2.4 | N1 | 6.1672 | 1.1914 | N | 8.816 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 22.09 | 4.94 | N2 | 22.2952 | 4.0565 | N1 | 22.0875 | 4.9378 | N | 33.9672 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 2.35 | 1.41 | N2 | 2.7478 | 0.6753 | N1 | 2.346 | 1.4112 | N | 3.5167 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 5.64 | 1.45 | N2 | 5.8562 | 1.143 | N1 | 5.6364 | 1.4543 | N | 5.9847 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 1.46 | 2.13 | N2 | 1.5212 | 1.0409 | N1 | 1.4649 | 2.1305 | N | 1.6258 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.08 | 1.31 | N2 | 2.1003 | 1.3065 | N1 | 2.0827 | 1.3079 | N | 2.5536 | 20.21 | 0 | 0.1 | 0 | 0 | 0 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 2.29 | 1.87 | N2 | 2.4255 | 0.25637 | N1 | 2.2881 | 1.8693 | N | 2.288 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 3.45 | 3.75 | N2 | 3.5153 | 1.1486 | N1 | 3.4523 | 3.7453 | N | 6.2648 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 3.32 | 4.17 | N2 | 3.5638 | 0.76504 | N1 | 3.3164 | 4.1672 | N | 3.3504 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 23.46 | 18.5 | N2 | 23.4843 | 18.4931 | N1 | 23.4569 | 18.5001 | N | 89.215 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 2.02 | 0.59 | N2 | 2.33 | 1.3797 | N1 | 2.0239 | 0.58712 | N | 3.8058 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 4.1 | 1.42 | N2 | 4.13 | 1.4173 | N1 | 4.0976 | 1.418 | N | 7.7245 | 117.1216 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.47 | 0.72 | N2 | 0.56036 | 1.0014 | N1 | 0.46822 | 0.72302 | N | 0.51361 | 4.2311 | 0 | 0 | 0 | 0 | 0.1 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 2.27 | 3 | N2 | 2.2878 | 0.60933 | N1 | 2.2744 | 2.9986 | N | 3.7229 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 2.28 | 0.38 | N2 | 2.2999 | 0.38384 | N1 | 2.2768 | 0.38403 | N | 3.087 | 31.7154 | 0 | 0.1 | 0 | 0 | 0 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 3.22 | 0.94 | N2 | 3.2498 | 0.93808 | N1 | 3.2219 | 0.93854 | N | 5.4835 | 77.5201 | 0 | 0.1 | 0 | 0 | 0 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 4.82 | 6.79 | N2 | 4.9 | 2.9632 | N1 | 4.8164 | 6.7941 | N | 5.7595 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 1.51 | 1.31 | N2 | 1.5786 | 1.2452 | N1 | 1.5122 | 1.3116 | N | 1.7149 | 10.3845 | 0 | 0.2 | 0 | 0 | 0 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 5.9 | 6.72 | N2 | 5.9371 | 1.2726 | N1 | 5.9001 | 6.7152 | N | 9.0462 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 2.83 | 0.69 | N2 | 2.8585 | 0.68975 | N1 | 2.8326 | 0.69009 | N | 4.5217 | 56.997 | 0 | 0.1 | 0 | 0 | 0 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.08 | 2.15 | N2 | 1.2836 | 0.24519 | N1 | 1.0767 | 2.1538 | N | 1.2466 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 23.93 | 0.22 | N2 | 27.0976 | 0.30895 | N1 | 23.9329 | 0.21612 | N | 49.9453 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.15 | 1.24 | N2 | 1.3614 | 0.26409 | N1 | 1.1532 | 1.2412 | N | 1.489 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 47.7 | 48.29 | N2 | 53.5125 | 1.0828 | N1 | 47.7038 | 48.291 | N | 47.9285 | 67.664 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.13 | 0.83 | N2 | 1.3115 | 1.1177 | N1 | 1.1283 | 0.82521 | N | 1.3707 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 3.43 | 0.6 | N2 | 3.4483 | 0.60246 | N1 | 3.4278 | 0.60258 | N | 5.0678 | 51.9745 | 0 | 0.1 | 0 | 0 | 0 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 3.76 | 5.31 | N2 | 3.9506 | 1.7351 | N1 | 3.76 | 5.3129 | N | 3.9533 | 14.485 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 3.41 | 1.56 | N2 | 3.6425 | 1.1034 | N1 | 3.4062 | 1.5584 | N | 3.5605 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 4.63 | 6.33 | N2 | 4.6777 | 0.33551 | N1 | 4.6342 | 6.3276 | N | 5.0713 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 3.51 | 0.29 | N2 | 3.5205 | 0.2877 | N1 | 3.5106 | 0.28796 | N | 4.3159 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 7.43 | 2.47 | N2 | 7.4832 | 2.4682 | N1 | 7.4329 | 2.4687 | N | 14.9193 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 6.52 | 0.86 | N2 | 6.5212 | 0.8618 | N1 | 6.5194 | 0.86207 | N | 7.5438 | 46.0638 | 0 | 0 | 0 | 0 | 0 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 3.76 | 0.96 | N2 | 3.7557 | 0.95816 | N1 | 3.8605 | 0.7577 | N | 6.2128 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 3.22 | 0.59 | N2 | 3.7557 | 0.95816 | N1 | 3.2216 | 0.59124 | N | 5.1645 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.3 | 0.8 | N2 | 1.3094 | 0.29539 | N1 | 1.2987 | 0.79952 | N | 1.943 | 24.2723 | 0 | 0 | 0 | 0 | 0.1 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 1.52 | 0.69 | N2 | 1.5329 | 0.68598 | N1 | 1.5228 | 0.68633 | N | 3.1897 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 9.45 | 9.26 | N2 | 9.9083 | 0.95152 | N1 | 9.4512 | 9.2616 | N | 11.5896 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 0.98 | 1.23 | N2 | 1.032 | 0.59335 | N1 | 0.97863 | 1.2265 | N | 1.0392 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 2.94 | 0.82 | N2 | 2.9623 | 0.8243 | N1 | 2.9359 | 0.8247 | N | 5.0677 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 0.98 | 1.77 | N2 | 1.1647 | 1.5594 | N1 | 0.976 | 1.7704 | N | 1.2074 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 4.23 | 0.57 | N2 | 4.396 | 0.43613 | N1 | 4.2312 | 0.57173 | N | 5.2041 | 35.8672 | 0 | 0.2 | 0 | 0 | 0 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 2.02 | 0.36 | N2 | 2.3279 | 0.42251 | N1 | 2.0175 | 0.36159 | N | 2.7594 | 34.713 | 0 | 0 | 0 | 0 | 0 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-2 | 7.34 | 1.41 | N2 | 7.3369 | 1.4126 | N1 | 7.3524 | 3.5333 | N | 10.5975 | 118.5846 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 7.64 | 1.46 | N2 | 7.6951 | 1.461 | N1 | 7.6434 | 1.4618 | N | 11.0356 | 120.6742 | 0 | 0.1 | 0 | 0 | 0 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.45 | 1.27 | N2 | 0.57082 | 0.10523 | N1 | 0.46309 | 1.0556 | N | 0.4546 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 0.76 | 1.61 | N2 | 0.88557 | 0.76487 | N1 | 0.75744 | 1.6136 | N | 0.80424 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 3.53 | 1.08 | N2 | 3.5592 | 1.0842 | N1 | 3.5298 | 1.0847 | N | 6.1689 | 89.5966 | 0 | 0.1 | 0 | 0 | 0 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 11.47 | 4.07 | N2 | 11.5383 | 4.0714 | N1 | 11.4652 | 4.0722 | N | 25.5652 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.1 | 1.69 | N2 | 1.1375 | 1.3437 | N1 | 1.0979 | 1.6852 | N | 1.3311 | 10.8753 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 4.44 | 1.16 | N2 | 4.602 | 0.75361 | N1 | 4.4369 | 1.1622 | N | 6.4982 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 22.71 | 2.71 | N2 | 23.4508 | 0.99624 | N1 | 22.7071 | 2.7119 | N | 25.2774 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 8.8 | 7.74 | N2 | 8.8115 | 7.7353 | N1 | 8.7951 | 7.7367 | N | 32.8625 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 5.43 | 1.06 | N2 | 5.5956 | 0.46723 | N1 | 5.4313 | 1.0615 | N | 6.4324 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 4.8 | 1.95 | N2 | 4.8385 | 1.9525 | N1 | 4.8026 | 1.9529 | N | 10.6276 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 3.17 | 3.35 | N2 | 3.1841 | 3.3477 | N1 | 3.1736 | 3.3507 | N | 4.3056 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 3.1 | 1.6 | N2 | 3.2245 | 1.4824 | N1 | 3.0995 | 1.5996 | N | 3.2422 | 12.4713 | 0 | 0.2 | 0 | 0 | 0 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 5.1 | 6.39 | N2 | 5.13 | 0.60106 | N1 | 5.0977 | 6.3925 | N | 6.1417 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 4.47 | 1.21 | N2 | 5.1043 | 1.7985 | N1 | 4.4669 | 1.2061 | N | 7.486 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.18 | 1.89 | N2 | 1.2073 | 1.0924 | N1 | 1.1836 | 1.8918 | N | 1.5863 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 12.45 | 1.42 | N2 | 12.5313 | 1.4226 | N1 | 12.4513 | 1.4236 | N | 14.1004 | 82.1605 | 0 | 0.1 | 0 | 0 | 0 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 20.12 | 0.19 | N2 | 20.1203 | 0.19398 | N1 | 20.1202 | 0.19399 | N | 37.2304 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.26 | 2.08 | N2 | 1.4541 | 0.71637 | N1 | 1.2607 | 2.0771 | N | 1.4681 | 10.6592 | 0 | 0 | 0 | 0 | 0.3 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 3.28 | 4.28 | N2 | 3.4282 | 0.61406 | N1 | 3.283 | 4.2811 | N | 3.283 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 8.5 | 3.19 | N2 | 8.4996 | 3.1938 | N1 | 8.4974 | 3.1945 | N | 17.9495 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 12.12 | 0.86 | N2 | 12.1196 | 0.85741 | N1 | 12.119 | 0.85754 | N | 16.2028 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 14.1 | 0.85 | N2 | 14.1259 | 0.85006 | N1 | 14.0955 | 0.85021 | N | 17.738 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 18.53 | 1.12 | N2 | 18.5301 | 1.1185 | N1 | 18.5288 | 1.1189 | N | 20.6858 | 76.5061 | 0 | 0 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 6.85 | 2.42 | N2 | 6.8989 | 2.4242 | N1 | 6.8518 | 2.4246 | N | 14.3039 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 2.94 | 3.66 | N2 | 3.1036 | 1.202 | N1 | 2.9413 | 3.66 | N | 3.063 | 9.9085 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 4.61 | 0.92 | N2 | 4.7877 | 0.68442 | N1 | 4.6126 | 0.91564 | N | 6.0964 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.04 | 1.26 | N2 | 1.0579 | 1.8897 | N1 | 1.0415 | 1.2632 | N | 1.3948 | 15.2973 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 14.37 | 32.5 | N2 | 14.384 | 32.4807 | N1 | 14.3701 | 32.4984 | N | 127.7676 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 35.14 | 155.19 | N2 | 35.255 | 155.1076 | N1 | 35.1392 | 155.1895 | N | 114.69 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 9.9 | 2.61 | N2 | 9.9633 | 2.6094 | N1 | 9.8989 | 2.6107 | N | 16.4039 | 215.5592 | 0 | 0.1 | 0 | 0 | 0 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 3.32 | 1.37 | N2 | 3.3533 | 1.3712 | N1 | 3.325 | 1.3719 | N | 6.7244 | 113.3242 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 7.93 | 0.85 | N2 | 8.3632 | 0.30116 | N1 | 7.9318 | 0.84904 | N | 8.3595 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 18.27 | 1.68 | N2 | 18.3048 | 1.6818 | N1 | 18.2728 | 1.683 | N | 19.7685 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 6.56 | 1.7 | N2 | 6.6838 | 1.4217 | N1 | 6.5553 | 1.7012 | N | 6.8759 | 22.5424 | 0 | 0.1 | 0 | 0 | 0 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 4.3 | 2.76 | N2 | 4.3076 | 2.7591 | N1 | 4.2955 | 2.7596 | N | 12.75 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 2.65 | 4.09 | N2 | 2.8052 | 1.2593 | N1 | 2.6535 | 4.0889 | N | 2.7934 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 6.81 | 11.88 | N2 | 7.2419 | 1.4548 | N1 | 6.8134 | 11.8764 | N | 6.8134 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 0.92 | 0.85 | N2 | 1.0101 | 0.10098 | N1 | 0.9163 | 0.84687 | N | 0.91622 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 10.64 | 2.55 | N2 | 10.7122 | 2.55 | N1 | 10.6435 | 2.5513 | N | 17.7322 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 9.39 | 5.84 | N2 | 9.4459 | 5.8401 | N1 | 9.3852 | 5.8412 | N | 27.3624 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.15 | 4.99 | N2 | 1.4088 | 0.2836 | N1 | 1.1571 | 1.5589 | N | 1.1511 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 11.81 | 6.18 | N2 | 12.2992 | 2.3893 | N1 | 11.8147 | 6.1822 | N | 19.1552 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 4.29 | 1.21 | N2 | 4.5377 | 1.0064 | N1 | 4.2905 | 1.2096 | N | 4.571 | 16.6658 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 1.74 | 1.3 | N2 | 1.7487 | 1.2977 | N1 | 1.7385 | 1.2984 | N | 2.1439 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 2.32 | 1.07 | N2 | 2.5054 | 0.71611 | N1 | 2.3217 | 1.072 | N | 2.3994 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25lcostcoef130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0322
exponent_for_line_cost_function | 0.6398
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 13.31 | 20.69 | N2 | 13.5201 | 0.69847 | N1 | 13.3108 | 20.6949 | N | 14.1883 | 49.968 | 0 | 0 | 0 | 0 | 0.3 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 12.63 | 6.59 | N2 | 12.6395 | 6.5904 | N1 | 12.6268 | 6.593 | N | 15.2571 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 6.05 | 1.26 | N2 | 6.3957 | 0.41721 | N1 | 6.052 | 1.2629 | N | 6.9541 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 3.29 | 11.35 | N2 | 4.2542 | 1.0303 | N1 | 3.3733 | 11.3505 | N | 3.2881 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 36.3 | 5.64 | N2 | 41.6113 | 0.5367 | N1 | 36.2956 | 5.638 | N | 59.5338 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 9.2 | 10.67 | N2 | 9.336 | 2.0877 | N1 | 9.196 | 10.6702 | N | 14.8689 | 197.4535 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 4.3 | 3.43 | N2 | 4.4045 | 0.74876 | N1 | 4.303 | 3.4257 | N | 5.9074 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-0 | 2.24 | 23.29 | N2 | 2.3937 | 2.9978 | N1 | 2.2425 | 23.2903 | N | 2.2424 | 23.2903 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 3.38 | 14.16 | N2 | 3.5674 | 5.6209 | N1 | 3.3779 | 14.1599 | N | 3.3946 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.82 | 0.85 | N2 | 2.8413 | 0.85392 | N1 | 2.8162 | 0.85434 | N | 5.2085 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 15.82 | 11.85 | N2 | 18.9067 | 1.6117 | N1 | 15.8193 | 11.846 | N | 17.5142 | 128.9274 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 11.25 | 1.19 | N2 | 13.0853 | 2.4 | N1 | 11.2473 | 1.1914 | N | 12.8801 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 39.23 | 4.94 | N2 | 39.6807 | 4.0565 | N1 | 39.228 | 4.9378 | N | 50.2915 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 4.19 | 3.44 | N2 | 4.9773 | 0.6753 | N1 | 4.1862 | 3.4388 | N | 5.0607 | 47.103 | 0 | 0 | 0 | 0 | 0.3 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 10.05 | 1.45 | N2 | 10.4644 | 1.143 | N1 | 10.0538 | 1.4543 | N | 10.2254 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.6 | 3.35 | N2 | 2.753 | 1.0409 | N1 | 2.6019 | 3.3518 | N | 2.7208 | 8.2264 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 3.61 | 2.56 | N2 | 3.6621 | 1.3065 | N1 | 3.6126 | 2.5577 | N | 3.9909 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 4.01 | 1.87 | N2 | 4.2974 | 0.25637 | N1 | 4.0106 | 1.8693 | N | 4.0106 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 6.19 | 3.75 | N2 | 6.3831 | 1.1486 | N1 | 6.1926 | 3.7453 | N | 8.8139 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 5.8 | 4.17 | N2 | 6.3461 | 0.76504 | N1 | 5.7992 | 4.1672 | N | 5.8126 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 40.97 | 18.5 | N2 | 40.9945 | 18.4931 | N1 | 40.9672 | 18.5001 | N | 105.3783 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 3.49 | 0.59 | N2 | 4.031 | 1.3797 | N1 | 3.4899 | 0.58712 | N | 4.9786 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 7.11 | 6.98 | N2 | 7.2383 | 1.4173 | N1 | 7.1057 | 6.985 | N | 10.4753 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-0 | 0.8 | 4.23 | N2 | 0.97666 | 1.0014 | N1 | 0.81734 | 0.83304 | N | 0.80189 | 4.2311 | 0 | 0 | 0 | 0 | 0 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 4.03 | 3 | N2 | 4.1284 | 0.60933 | N1 | 4.0332 | 2.9986 | N | 5.3589 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 3.94 | 3.67 | N2 | 4.0075 | 0.38384 | N1 | 3.9373 | 3.6667 | N | 4.5981 | 31.7154 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 5.56 | 4.77 | N2 | 5.6851 | 0.93808 | N1 | 5.5564 | 4.771 | N | 7.6386 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 8.45 | 6.79 | N2 | 8.6336 | 2.9632 | N1 | 8.4509 | 6.7941 | N | 9.0636 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.62 | 3.5 | N2 | 2.7694 | 1.2452 | N1 | 2.6187 | 3.504 | N | 2.7687 | 10.3845 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 10.17 | 6.72 | N2 | 10.4064 | 1.2726 | N1 | 10.1707 | 6.7152 | N | 13.0188 | 105.0419 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 4.88 | 3.87 | N2 | 4.9939 | 0.68975 | N1 | 4.8787 | 3.8736 | N | 6.4115 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.9 | 2.15 | N2 | 2.3405 | 0.24519 | N1 | 1.9001 | 2.1538 | N | 1.9785 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 41.54 | 6.83 | N2 | 47.5589 | 0.30895 | N1 | 41.5412 | 6.8341 | N | 64.1146 | 335.5287 | 0 | 0 | 0 | 0 | 0.1 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 2.03 | 2.06 | N2 | 2.4231 | 0.26409 | N1 | 2.0269 | 2.0573 | N | 2.2243 | 15.4837 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 84.97 | 57.28 | N2 | 97.8893 | 1.0828 | N1 | 84.9725 | 57.2802 | N | 85.164 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 2.01 | 2.11 | N2 | 2.3356 | 1.1177 | N1 | 2.0082 | 2.1133 | N | 2.0799 | 13.2034 | 0 | 0 | 0 | 0 | 0.1 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 5.28 | 4.55 | N2 | 5.391 | 0.60246 | N1 | 5.2792 | 4.5481 | N | 6.787 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 6.52 | 8.66 | N2 | 7.0134 | 1.7351 | N1 | 6.5228 | 8.6578 | N | 6.6637 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 6.07 | 8.07 | N2 | 6.514 | 1.1034 | N1 | 6.0658 | 8.0671 | N | 6.1017 | 10.5275 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 8.04 | 6.33 | N2 | 8.2563 | 0.33551 | N1 | 8.0371 | 6.3276 | N | 8.3644 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 6.42 | 0.29 | N2 | 6.425 | 0.2877 | N1 | 6.4151 | 0.28796 | N | 7.1042 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 13.08 | 2.47 | N2 | 13.1601 | 2.4682 | N1 | 13.0847 | 2.4687 | N | 19.9431 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 10.01 | 7.62 | N2 | 10.1096 | 0.8618 | N1 | 10.0068 | 7.6165 | N | 10.7336 | 46.0638 | 0 | 0 | 0 | 0 | 0.2 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 5.87 | 0.96 | N2 | 5.8704 | 0.95816 | N1 | 6.0932 | 7.4825 | N | 8.0842 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 5.04 | 0.59 | N2 | 5.8704 | 0.95816 | N1 | 5.044 | 0.59124 | N | 6.6224 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 2.28 | 1.69 | N2 | 2.3266 | 0.29539 | N1 | 2.2757 | 1.6928 | N | 2.8472 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.72 | 0.69 | N2 | 2.7295 | 0.68598 | N1 | 2.7195 | 0.68633 | N | 4.2534 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 16.72 | 9.26 | N2 | 17.794 | 0.40216 | N1 | 16.7231 | 9.2616 | N | 18.5707 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.7 | 2.17 | N2 | 1.8071 | 0.59335 | N1 | 1.6965 | 2.1674 | N | 1.7251 | 4.884 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 5.14 | 0.82 | N2 | 5.1746 | 0.8243 | N1 | 5.1384 | 0.8247 | N | 7.0255 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.72 | 1.77 | N2 | 2.0755 | 1.5594 | N1 | 1.717 | 1.7704 | N | 1.8381 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 7.35 | 5.85 | N2 | 7.7871 | 0.43613 | N1 | 7.3548 | 5.851 | N | 8.2051 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 3.59 | 2.23 | N2 | 4.2085 | 0.42251 | N1 | 3.5905 | 2.2316 | N | 4.0617 | 34.713 | 0 | 0 | 0 | 0 | 0.2 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 12.77 | 14.48 | N2 | 12.9397 | 1.4126 | N1 | 12.7722 | 14.4819 | N | 15.5557 | 118.5846 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 13.27 | 9.96 | N2 | 13.5744 | 1.461 | N1 | 13.2701 | 9.9648 | N | 16.2385 | 120.6742 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.74 | 1.27 | N2 | 0.98648 | 0.10523 | N1 | 0.75682 | 1.0556 | N | 0.74116 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-0 | 1.29 | 6.87 | N2 | 1.59 | 0.76487 | N1 | 1.3263 | 6.8747 | N | 1.292 | 6.8747 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 6.1 | 5.5 | N2 | 6.2323 | 1.0842 | N1 | 6.0992 | 5.5017 | N | 8.5345 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 20.18 | 4.07 | N2 | 20.2922 | 4.0714 | N1 | 20.1803 | 4.0722 | N | 33.312 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.87 | 2.5 | N2 | 1.9654 | 1.3437 | N1 | 1.8716 | 2.4993 | N | 2.0637 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 7.83 | 1.16 | N2 | 8.1456 | 0.75361 | N1 | 7.8341 | 1.1622 | N | 9.634 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 40.59 | 2.71 | N2 | 42.105 | 0.99624 | N1 | 40.5887 | 2.7119 | N | 42.4438 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 15.29 | 7.74 | N2 | 15.3089 | 7.7353 | N1 | 15.2926 | 7.7367 | N | 38.638 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 9.65 | 1.06 | N2 | 9.9579 | 0.46723 | N1 | 9.6464 | 1.0615 | N | 10.4467 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 8.41 | 6.01 | N2 | 8.4774 | 1.9525 | N1 | 8.4083 | 6.0093 | N | 13.8478 | 184.6689 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 5.78 | 3.35 | N2 | 5.7943 | 3.3477 | N1 | 5.7838 | 3.3507 | N | 6.7149 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 5.35 | 8.29 | N2 | 5.7163 | 1.4824 | N1 | 5.3534 | 8.2898 | N | 5.4473 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 8.83 | 6.39 | N2 | 9.0556 | 0.60106 | N1 | 8.8307 | 6.3925 | N | 9.7542 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 7.74 | 7.18 | N2 | 8.9652 | 1.7985 | N1 | 7.7372 | 7.1819 | N | 10.1478 | 119.458 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 2.08 | 1.89 | N2 | 2.1476 | 1.0924 | N1 | 2.0821 | 1.8918 | N | 2.422 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 21.36 | 31.58 | N2 | 22.1725 | 1.4226 | N1 | 21.3574 | 31.5849 | N | 22.6324 | 82.1605 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 35.3 | 8.57 | N2 | 35.3119 | 0.19398 | N1 | 35.3049 | 8.5716 | N | 50.734 | 212.9358 | 0 | 0 | 0 | 0 | 0.1 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 2.2 | 2.65 | N2 | 2.6354 | 0.71637 | N1 | 2.2032 | 2.6538 | N | 2.2861 | 10.6592 | 0 | 0 | 0 | 0 | 0.4 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 5.94 | 4.28 | N2 | 6.3084 | 0.61406 | N1 | 5.9417 | 4.2811 | N | 5.9416 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 13.01 | 3.19 | N2 | 13.0097 | 3.1938 | N1 | 13.0075 | 3.1945 | N | 21.9584 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 17.69 | 0.86 | N2 | 17.6861 | 0.85741 | N1 | 17.6855 | 0.85754 | N | 21.4941 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 20.41 | 0.85 | N2 | 20.4504 | 0.85006 | N1 | 20.41 | 0.85021 | N | 23.7998 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 29.93 | 7.56 | N2 | 30.106 | 1.1185 | N1 | 29.9311 | 7.5573 | N | 31.6895 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 12.04 | 15.51 | N2 | 12.1234 | 2.4242 | N1 | 12.0442 | 15.514 | N | 18.9274 | 229.282 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 5.1 | 5.92 | N2 | 5.5077 | 1.202 | N1 | 5.099 | 5.9183 | N | 5.1905 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 8.16 | 0.92 | N2 | 8.4835 | 0.68442 | N1 | 8.1557 | 0.91564 | N | 9.367 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.76 | 2.95 | N2 | 1.8086 | 1.8897 | N1 | 1.7611 | 2.9473 | N | 2.0591 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 24.63 | 32.5 | N2 | 24.6458 | 32.4807 | N1 | 24.632 | 32.4984 | N | 137.211 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 61.79 | 155.19 | N2 | 61.9708 | 155.1076 | N1 | 61.7922 | 155.1895 | N | 139.7752 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 17.24 | 15.24 | N2 | 17.5677 | 2.6094 | N1 | 17.243 | 15.2431 | N | 23.1334 | 215.5592 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 5.79 | 3.46 | N2 | 5.8585 | 1.3712 | N1 | 5.7863 | 3.4583 | N | 8.9413 | 113.3242 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 14.02 | 17.75 | N2 | 14.9619 | 0.30116 | N1 | 14.0194 | 17.7462 | N | 14.199 | 27.6312 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 31.65 | 60.18 | N2 | 32.249 | 1.6818 | N1 | 31.6546 | 60.1784 | N | 32.1633 | 96.7024 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 11.45 | 12.36 | N2 | 11.8851 | 1.4217 | N1 | 11.4501 | 12.3577 | N | 11.6623 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 7.78 | 2.76 | N2 | 7.7907 | 2.7591 | N1 | 7.7786 | 2.7596 | N | 15.8461 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 4.63 | 4.09 | N2 | 4.9709 | 1.2593 | N1 | 4.6339 | 4.0889 | N | 4.7099 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 11.89 | 11.88 | N2 | 12.975 | 1.4548 | N1 | 11.8869 | 11.8764 | N | 11.8869 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.6 | 0.85 | N2 | 1.7862 | 0.10098 | N1 | 1.6031 | 0.84687 | N | 1.6031 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 18.78 | 2.55 | N2 | 18.8892 | 2.55 | N1 | 18.7843 | 2.5513 | N | 24.9685 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 16.46 | 5.84 | N2 | 16.5538 | 5.8401 | N1 | 16.4616 | 5.8412 | N | 33.6526 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 1.96 | 4.99 | N2 | 2.5711 | 0.2836 | N1 | 2.0066 | 4.9655 | N | 1.956 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 20.92 | 6.18 | N2 | 21.9781 | 2.3893 | N1 | 20.9154 | 6.1822 | N | 27.7206 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 7.53 | 8.86 | N2 | 8.0898 | 1.0064 | N1 | 7.53 | 8.8597 | N | 7.7144 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 3.14 | 1.3 | N2 | 3.1459 | 1.2977 | N1 | 3.1357 | 1.2984 | N | 3.3858 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 4.13 | 3.52 | N2 | 4.4741 | 0.07716 | N1 | 4.1338 | 3.5196 | N | 4.1486 | 6.2109 | 0 | 0.5 | 0 | 0 | 0.1 | 0

## oq25lcostexp70
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.4483
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 5.3 | 0.7 | N2 | 5.3108 | 0.69847 | N1 | 5.2977 | 0.69908 | N | 6.6105 | 49.968 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 5.07 | 6.59 | N2 | 5.0858 | 6.5904 | N1 | 5.0731 | 6.593 | N | 8.2845 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 3.43 | 1.26 | N2 | 3.6055 | 0.41721 | N1 | 3.4285 | 1.2629 | N | 4.4849 | 39.0871 | 0 | 0.3 | 0 | 0 | 0 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-1 | 2.18 | 2.8 | N2 | 3.0131 | 1.0303 | N1 | 2.1779 | 2.8048 | N | 2.1972 | 11.3505 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 11.23 | 0.27 | N2 | 13.8664 | 0.5367 | N1 | 11.225 | 0.27224 | N | 39.3719 | 332.2442 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 4.02 | 2.09 | N2 | 4.0528 | 2.0877 | N1 | 4.0199 | 2.088 | N | 10.1935 | 197.4535 | 0 | 0.1 | 0 | 0 | 0 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 2.2 | 0.75 | N2 | 2.2123 | 0.74876 | N1 | 2.2017 | 0.74915 | N | 3.9587 | 61.5252 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 1.41 | 7.55 | N2 | 1.4796 | 2.9978 | N1 | 1.4086 | 7.5519 | N | 1.4334 | 23.2903 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 1.9 | 14.16 | N2 | 1.9779 | 5.6209 | N1 | 1.9008 | 14.1599 | N | 1.9878 | 43.6692 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 1.7 | 0.85 | N2 | 1.7235 | 0.85392 | N1 | 1.7033 | 0.85434 | N | 4.2193 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 6.63 | 3.98 | N2 | 8.718 | 1.6117 | N1 | 6.6256 | 3.9777 | N | 9.8102 | 128.9274 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 4.92 | 1.19 | N2 | 6.5491 | 2.4 | N1 | 4.9244 | 1.1914 | N | 7.8218 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 14.24 | 4.94 | N2 | 14.3313 | 4.0565 | N1 | 14.2358 | 4.9378 | N | 26.4894 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 1.83 | 1.41 | N2 | 2.4041 | 0.6753 | N1 | 1.8272 | 1.4112 | N | 3.0844 | 47.103 | 0 | 0 | 0 | 0 | 0.2 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 5.43 | 1.45 | N2 | 5.6418 | 0.26671 | N1 | 5.4315 | 1.4543 | N | 5.7881 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 1.51 | 2.13 | N2 | 1.5737 | 1.0409 | N1 | 1.5139 | 2.1305 | N | 1.6725 | 8.2264 | 0 | 0 | 0 | 0 | 0.3 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 2.23 | 1.31 | N2 | 2.2439 | 1.3065 | N1 | 2.2259 | 1.3079 | N | 2.6858 | 20.21 | 0 | 0.1 | 0 | 0 | 0 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 2.33 | 1.87 | N2 | 2.4733 | 0.25637 | N1 | 2.332 | 1.8693 | N | 2.3319 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 2.83 | 3.75 | N2 | 2.8625 | 1.1486 | N1 | 2.8285 | 3.7453 | N | 5.6845 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 3.08 | 4.17 | N2 | 3.2983 | 0.76504 | N1 | 3.0796 | 4.1672 | N | 3.1155 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 13.71 | 18.5 | N2 | 13.7355 | 18.4931 | N1 | 13.7081 | 18.5001 | N | 80.2161 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 1.72 | 0.59 | N2 | 2.2155 | 1.3797 | N1 | 1.7249 | 0.58712 | N | 3.5667 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 3.33 | 1.42 | N2 | 3.3566 | 1.4173 | N1 | 3.3277 | 1.418 | N | 7.0402 | 117.1216 | 0 | 0.1 | 0 | 0 | 0 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.57 | 0.72 | N2 | 0.77126 | 1.0014 | N1 | 0.57366 | 0.72302 | N | 0.59969 | 4.2311 | 0 | 0 | 0 | 0 | 0.1 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 2.1 | 0.61 | N2 | 2.1142 | 0.60933 | N1 | 2.1037 | 0.60964 | N | 3.5686 | 50.0656 | 0 | 0 | 0 | 0 | 0 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 2.16 | 0.38 | N2 | 2.1829 | 0.38384 | N1 | 2.1603 | 0.38403 | N | 2.9834 | 31.7154 | 0 | 0.1 | 0 | 0 | 0 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 2.79 | 0.94 | N2 | 2.8132 | 0.93808 | N1 | 2.7873 | 0.93854 | N | 5.0972 | 77.5201 | 0 | 0.1 | 0 | 0 | 0 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 3.73 | 6.79 | N2 | 3.7881 | 2.9632 | N1 | 3.734 | 6.7941 | N | 4.7756 | 244.907 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 1.75 | 2.09 | N2 | 1.8339 | 1.2452 | N1 | 1.7532 | 2.0923 | N | 1.9409 | 10.3845 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 4.38 | 1.27 | N2 | 4.3978 | 1.2726 | N1 | 4.3844 | 1.2732 | N | 7.6779 | 105.0419 | 0 | 0 | 0 | 0 | 0 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 2.54 | 0.69 | N2 | 2.5603 | 0.68975 | N1 | 2.5357 | 0.69009 | N | 4.2579 | 56.997 | 0 | 0.1 | 0 | 0 | 0 | 0
| 32 | 8.41 | 32848.83 | 0 | 1 | N-1 | 1.03 | 2.15 | N2 | 1.3886 | 0.24519 | N1 | 1.0289 | 2.1538 | N | 1.2041 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 12.45 | 0.22 | N2 | 15.3331 | 0.30895 | N1 | 12.4465 | 0.21612 | N | 40.7561 | 335.5287 | 0 | 0 | 0 | 0 | 0 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 1.1 | 1.24 | N2 | 1.465 | 0.26409 | N1 | 1.1007 | 1.2412 | N | 1.4452 | 15.4837 | 0 | 0 | 0 | 0 | 0.2 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 30.49 | 2.08 | N2 | 32.9041 | 0.38061 | N1 | 30.4948 | 2.0848 | N | 31.4106 | 67.664 | 0 | 0.3 | 0 | 0 | 0 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 1.09 | 0.83 | N2 | 1.4255 | 1.1177 | N1 | 1.0861 | 0.82521 | N | 1.337 | 13.2034 | 0 | 0 | 0 | 0 | 0 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 2.6 | 0.6 | N2 | 2.6132 | 0.60246 | N1 | 2.5964 | 0.60258 | N | 4.3288 | 51.9745 | 0 | 0.1 | 0 | 0 | 0 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 3.41 | 5.31 | N2 | 3.5654 | 1.7351 | N1 | 3.4078 | 5.3129 | N | 3.6125 | 14.485 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 3.59 | 1.56 | N2 | 3.7947 | 0.18804 | N1 | 3.5926 | 1.5584 | N | 3.738 | 10.5275 | 0 | 0.4 | 0 | 0 | 0 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 3.99 | 0.34 | N2 | 4.0168 | 0.33551 | N1 | 3.9907 | 0.3358 | N | 4.463 | 23.8144 | 0 | 0.1 | 0 | 0 | 0 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 3.81 | 0.29 | N2 | 3.8209 | 0.2877 | N1 | 3.811 | 0.28796 | N | 4.6043 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 5.17 | 2.47 | N2 | 5.2111 | 2.4682 | N1 | 5.171 | 2.4687 | N | 12.9087 | 233.451 | 0 | 0.1 | 0 | 0 | 0 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 4.53 | 0.86 | N2 | 4.5321 | 0.8618 | N1 | 4.5304 | 0.86207 | N | 5.7758 | 46.0638 | 0 | 0 | 0 | 0 | 0 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-1 | 2.8 | 0.76 | N2 | 2.8077 | 0.95816 | N1 | 2.8034 | 0.7577 | N | 5.3738 | 79.5468 | 0 | 0 | 0 | 0 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 2.24 | 0.59 | N2 | 2.8077 | 0.95816 | N1 | 2.2419 | 0.59124 | N | 4.3807 | 63.5878 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 1.41 | 0.8 | N2 | 1.4253 | 0.29539 | N1 | 1.412 | 0.79952 | N | 2.046 | 24.2723 | 0 | 0 | 0 | 0 | 0.1 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 1.59 | 0.69 | N2 | 1.5965 | 0.68598 | N1 | 1.5864 | 0.68633 | N | 3.2462 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 7.98 | 9.26 | N2 | 8.1074 | 0.40216 | N1 | 7.9847 | 9.2616 | N | 10.1818 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.27 | 1.23 | N2 | 1.3451 | 0.59335 | N1 | 1.2718 | 1.2265 | N | 1.3162 | 4.884 | 0 | 0.8 | 0 | 0 | 0.1 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 2.6 | 0.82 | N2 | 2.6295 | 0.8243 | N1 | 2.6046 | 0.8247 | N | 4.7732 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 0.97 | 1.77 | N2 | 1.3078 | 1.5594 | N1 | 0.97044 | 1.7704 | N | 1.2027 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 3.72 | 0.57 | N2 | 3.8636 | 0.43613 | N1 | 3.7207 | 0.57173 | N | 4.7329 | 35.8672 | 0 | 0.2 | 0 | 0 | 0 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 1.64 | 0.36 | N2 | 2.1375 | 0.42251 | N1 | 1.6371 | 0.36159 | N | 2.4551 | 34.713 | 0 | 0 | 0 | 0 | 0 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-2 | 5.11 | 1.41 | N2 | 5.1115 | 1.4126 | N1 | 5.1368 | 3.5333 | N | 8.6281 | 118.5846 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 5.25 | 1.46 | N2 | 5.2951 | 1.461 | N1 | 5.254 | 1.4618 | N | 8.9117 | 120.6742 | 0 | 0.1 | 0 | 0 | 0 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.54 | 1.27 | N2 | 0.78264 | 0.10523 | N1 | 0.55157 | 1.0556 | N | 0.54092 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-1 | 0.81 | 1.61 | N2 | 1.0707 | 0.76487 | N1 | 0.80624 | 1.6136 | N | 0.84577 | 6.8747 | 0 | 0 | 0 | 0 | 0.3 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 2.98 | 1.08 | N2 | 3.0075 | 1.0842 | N1 | 2.9805 | 1.0847 | N | 5.6807 | 89.5966 | 0 | 0.1 | 0 | 0 | 0 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 7.17 | 4.07 | N2 | 7.219 | 4.0714 | N1 | 7.165 | 4.0722 | N | 21.7429 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.25 | 1.69 | N2 | 1.3008 | 1.3437 | N1 | 1.2532 | 1.6852 | N | 1.4755 | 10.8753 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 3.86 | 1.16 | N2 | 3.9989 | 0.75361 | N1 | 3.8587 | 1.1622 | N | 5.9644 | 69.2747 | 0 | 0.2 | 0 | 0 | 0 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 15.03 | 2.71 | N2 | 15.4385 | 0.99624 | N1 | 15.0267 | 2.7119 | N | 17.9043 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 5.99 | 7.74 | N2 | 6.0074 | 7.7353 | N1 | 5.9911 | 7.7367 | N | 30.37 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 5.06 | 1.06 | N2 | 5.2103 | 0.46723 | N1 | 5.059 | 1.0615 | N | 6.0778 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 3.75 | 1.95 | N2 | 3.7792 | 1.9525 | N1 | 3.748 | 1.9529 | N | 9.6902 | 184.6689 | 0 | 0.1 | 0 | 0 | 0 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 2.94 | 3.35 | N2 | 2.9533 | 3.3477 | N1 | 2.9428 | 3.3507 | N | 4.0925 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 2.96 | 1.6 | N2 | 3.0764 | 1.4824 | N1 | 2.9575 | 1.5996 | N | 3.1111 | 12.4713 | 0 | 0.2 | 0 | 0 | 0 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 4.27 | 0.6 | N2 | 4.2995 | 0.60106 | N1 | 4.2724 | 0.60157 | N | 5.3775 | 42.7287 | 0 | 0.1 | 0 | 0 | 0 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 3.09 | 1.21 | N2 | 3.9211 | 1.7985 | N1 | 3.0913 | 1.2061 | N | 6.3856 | 119.458 | 0 | 0 | 0 | 0 | 0 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 1.31 | 1.89 | N2 | 1.3432 | 1.0924 | N1 | 1.3134 | 1.8918 | N | 1.707 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 7.53 | 1.42 | N2 | 7.5892 | 1.4226 | N1 | 7.5312 | 1.4236 | N | 9.7269 | 82.1605 | 0 | 0.1 | 0 | 0 | 0 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 12.22 | 0.19 | N2 | 12.2238 | 0.19398 | N1 | 12.2236 | 0.19399 | N | 30.2112 | 212.9358 | 0 | 0 | 0 | 0 | 0 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 1.17 | 2.08 | N2 | 1.5225 | 0.71637 | N1 | 1.17 | 2.0771 | N | 1.3909 | 10.6592 | 0 | 0 | 0 | 0 | 0.3 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 2.96 | 4.28 | N2 | 3.0834 | 0.61406 | N1 | 2.9647 | 4.2811 | N | 2.9646 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 5.81 | 3.19 | N2 | 5.8171 | 3.1938 | N1 | 5.8149 | 3.1945 | N | 15.565 | 280.1073 | 0 | 0 | 0 | 0 | 0 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 9.23 | 0.86 | N2 | 9.2303 | 0.85741 | N1 | 9.2298 | 0.85754 | N | 13.4564 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 10.66 | 0.85 | N2 | 10.6799 | 0.85006 | N1 | 10.655 | 0.85021 | N | 14.4351 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 12.7 | 1.12 | N2 | 12.7007 | 1.1185 | N1 | 12.6993 | 1.1189 | N | 15.1445 | 76.5061 | 0 | 0 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 4.87 | 2.42 | N2 | 4.9086 | 2.4242 | N1 | 4.8704 | 2.4246 | N | 12.5427 | 229.282 | 0 | 0.1 | 0 | 0 | 0 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 2.84 | 3.66 | N2 | 2.9893 | 1.202 | N1 | 2.8369 | 3.66 | N | 2.9619 | 9.9085 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 3.97 | 0.92 | N2 | 4.1126 | 0.68442 | N1 | 3.9653 | 0.91564 | N | 5.4989 | 55.1908 | 0 | 0.2 | 0 | 0 | 0 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.22 | 1.26 | N2 | 1.2364 | 1.8897 | N1 | 1.2152 | 1.2632 | N | 1.5527 | 15.2973 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 9.73 | 2.81 | N2 | 9.7473 | 2.81 | N1 | 9.7311 | 2.81 | N | 124.1238 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 19.58 | 155.19 | N2 | 19.657 | 155.1076 | N1 | 19.5778 | 155.1895 | N | 100.044 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 6.38 | 2.61 | N2 | 6.4316 | 2.6094 | N1 | 6.3828 | 2.6107 | N | 13.2785 | 215.5592 | 0 | 0.1 | 0 | 0 | 0 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 2.86 | 1.37 | N2 | 2.8834 | 1.3712 | N1 | 2.8571 | 1.3719 | N | 6.3085 | 113.3242 | 0 | 0.1 | 0 | 0 | 0 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 6.29 | 0.85 | N2 | 6.6143 | 0.30116 | N1 | 6.2874 | 0.84904 | N | 6.8118 | 27.6312 | 0 | 0.3 | 0 | 0 | 0 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-1 | 10.16 | 1.68 | N2 | 10.1924 | 1.6818 | N1 | 10.1604 | 1.683 | N | 12.5574 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 5.49 | 1.7 | N2 | 5.593 | 1.4217 | N1 | 5.4887 | 1.7012 | N | 5.872 | 22.5424 | 0 | 0.1 | 0 | 0 | 0 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 3.32 | 2.76 | N2 | 3.3298 | 2.7591 | N1 | 3.3176 | 2.7596 | N | 11.8808 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 2.63 | 4.09 | N2 | 2.7793 | 1.2593 | N1 | 2.6298 | 4.0889 | N | 2.7705 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-1 | 5.64 | 1.67 | N2 | 5.9447 | 1.4548 | N1 | 5.6385 | 1.6726 | N | 5.6654 | 11.8764 | 0 | 0.3 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.29 | 0.85 | N2 | 1.4326 | 0.10098 | N1 | 1.2902 | 0.84687 | N | 1.2901 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 6.74 | 2.55 | N2 | 6.791 | 2.55 | N1 | 6.7397 | 2.5513 | N | 14.2622 | 210.6526 | 0 | 0.1 | 0 | 0 | 0 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 6.2 | 5.84 | N2 | 6.2465 | 5.8401 | N1 | 6.2 | 5.8412 | N | 24.5312 | 552.3665 | 0 | 0.1 | 0 | 0 | 0 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-1 | 1.08 | 0.92 | N2 | 1.483 | 0.2836 | N1 | 1.0758 | 0.91791 | N | 1.0793 | 4.9908 | 0 | 0 | 0 | 0 | 0.4 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 8.51 | 6.18 | N2 | 8.7884 | 2.3893 | N1 | 8.5137 | 6.1822 | N | 16.0484 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 4.02 | 1.21 | N2 | 4.2487 | 1.0064 | N1 | 4.0187 | 1.2096 | N | 4.3152 | 16.6658 | 0 | 0.3 | 0 | 0 | 0 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 1.74 | 1.3 | N2 | 1.7458 | 1.2977 | N1 | 1.7356 | 1.2984 | N | 2.1413 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 2.86 | 1.07 | N2 | 2.9872 | 0.07716 | N1 | 2.8568 | 1.072 | N | 2.9131 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## oq25lcostexp130
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 40
oh_line_life_in_yrs | 50
ug_cable_life_in_yrs | 45
discount_rate | 0.056
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.00557
failures_per_annum_per_100km_oh_line | 0.2901
failures_per_annum_per_100km_ug_cable | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp | 0.0944
exponent_for_transformer_cost_function | 0.6398
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.8325
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 15351
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 720 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 6579 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 111.5 | 0 | 3 | 2 | 150 | 0 | 0.49 | 36119 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 2 | 100 | 0 | 3 | 2 | 150 | 0 | 0.73 | 6050 | 1 | 0.998 | 0.996 | 0.99 | 0.976 | 0.882 | 0.844 | 0.77 | 0.662 | 0.392 | 0
| 3 | 25.8 | 2 | 4 | 2 | 150 | 0 | 0.57 | 34827 | 1 | 1 | 1 | 0.995 | 0.941 | 0.764 | 0.451 | 0.26 | 0.091 | 0.017 | 0
| 4 | 3.6 | 1 | 1 | 3 | 300 | 0 | 0.45 | 33793 | 1 | 1 | 1 | 0.994 | 0.71 | 0.356 | 0.141 | 0.055 | 0.022 | 0.022 | 0
| 5 | 361.6 | 3 | 1 | 0 | 15 | 1 | 0.55 | 90000 | 1 | 1 | 1 | 1 | 0.981 | 0.854 | 0.606 | 0.372 | 0.154 | 0.018 | 0
| 6 | 67.2 | 2 | 2 | 2 | 150 | 0 | 0.55 | 34024 | 1 | 1 | 1 | 0.995 | 0.942 | 0.737 | 0.382 | 0.138 | 0.032 | 0.018 | 0
| 7 | 22.2 | 0 | 2 | 2 | 150 | 0 | 0.54 | 33835 | 1 | 1 | 1 | 1 | 0.914 | 0.736 | 0.313 | 0.101 | 0.034 | 0.018 | 0
| 8 | 8 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 9 | 15 | 2 | 2 | 2 | 150 | 0 | 0.56 | 6050 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 10 | 10 | 2 | 2 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 11 | 38 | 2 | 1 | 3 | 300 | 0 | 0.48 | 34430 | 1 | 1 | 1 | 0.977 | 0.829 | 0.448 | 0.201 | 0.082 | 0.021 | 0.021 | 0
| 12 | 22 | 0 | 1 | 3 | 300 | 0 | 0.75 | 34430 | 1 | 1 | 1 | 1 | 0.996 | 0.97 | 0.826 | 0.774 | 0.562 | 0.135 | 0
| 13 | 435 | 4 | 5 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 14 | 27 | 0 | 1 | 2 | 150 | 0 | 0.5 | 35253 | 1 | 1 | 1 | 0.994 | 0.871 | 0.587 | 0.239 | 0.063 | 0.02 | 0.02 | 0
| 15 | 47.7 | 3 | 6 | 2 | 150 | 0 | 0.54 | 36373 | 1 | 1 | 1 | 1 | 0.884 | 0.742 | 0.388 | 0.129 | 0.034 | 0.018 | 0
| 16 | 10.7 | 0 | 2 | 2 | 150 | 0 | 0.38 | 38166 | 1 | 1 | 0.976 | 0.769 | 0.541 | 0.292 | 0.094 | 0.045 | 0.026 | 0.026 | 0
| 17 | 13 | 3 | 3 | 2 | 150 | 0 | 0.54 | 34357 | 1 | 1 | 1 | 1 | 0.92 | 0.652 | 0.391 | 0.2 | 0.064 | 0.018 | 0
| 18 | 17.3 | 3 | 3 | 2 | 150 | 0 | 0.24 | 34357 | 1 | 0.974 | 0.751 | 0.441 | 0.196 | 0.086 | 0.042 | 0.042 | 0.042 | 0.042 | 0
| 19 | 40 | 0 | 2 | 2 | 150 | 0 | 0.52 | 34357 | 1 | 1 | 1 | 0.995 | 0.904 | 0.651 | 0.246 | 0.076 | 0.019 | 0.019 | 0
| 20 | 30.2 | 2 | 3 | 2 | 150 | 0 | 0.43 | 33831 | 1 | 1 | 0.996 | 0.951 | 0.677 | 0.279 | 0.067 | 0.023 | 0.023 | 0.023 | 0
| 21 | 571 | 4 | 3 | 2 | 150 | 0 | 0.65 | 39575 | 1 | 1 | 1 | 1 | 1 | 0.971 | 0.739 | 0.282 | 0.079 | 0.015 | 0
| 22 | 17.6 | 2 | 1 | 2 | 150 | 0 | 0.9 | 37691 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.553 | 0
| 23 | 45.1 | 2 | 2 | 2 | 150 | 0 | 0.53 | 35547 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 24 | 2 | 0 | 1 | 2 | 150 | 0 | 0.62 | 34513 | 1 | 1 | 1 | 1 | 0.994 | 0.933 | 0.711 | 0.306 | 0.082 | 0.016 | 0
| 25 | 20 | 0 | 2 | 2 | 150 | 0 | 0.53 | 35460 | 1 | 1 | 1 | 0.995 | 0.94 | 0.67 | 0.326 | 0.101 | 0.033 | 0.019 | 0
| 26 | 17.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 35460 | 1 | 1 | 1 | 0.983 | 0.802 | 0.503 | 0.284 | 0.128 | 0.053 | 0.02 | 0
| 27 | 30.8 | 2 | 2 | 2 | 150 | 0 | 0.54 | 34721 | 1 | 1 | 1 | 1 | 0.986 | 0.647 | 0.275 | 0.074 | 0.033 | 0.018 | 0
| 28 | 60 | 2 | 2 | 2 | 150 | 0 | 0.61 | 6050 | 1 | 0.999 | 0.997 | 0.993 | 0.97 | 0.918 | 0.622 | 0.332 | 0.248 | 0.016 | 0
| 29 | 8 | 2 | 3 | 2 | 150 | 0 | 0.54 | 34432 | 1 | 1 | 1 | 1 | 0.934 | 0.637 | 0.348 | 0.145 | 0.049 | 0.018 | 0
| 30 | 80 | 3 | 2 | 2 | 150 | 0 | 0.47 | 36683 | 1 | 1 | 1 | 0.988 | 0.812 | 0.396 | 0.134 | 0.053 | 0.021 | 0.021 | 0
| 31 | 25.1 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36353 | 1 | 1 | 1 | 0.985 | 0.875 | 0.607 | 0.333 | 0.135 | 0.035 | 0.019 | 0
| 32 | 8.4 | 0 | 1 | 2 | 150 | 0 | 0.37 | 32849 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 33 | 446 | 3 | 1 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 34 | 8.5 | 0 | 1 | 2 | 150 | 0 | 0.53 | 38350 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 35 | 313.1 | 2 | 4 | 1 | 30 | 1 | 0.46 | 40650 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 36 | 8 | 0 | 1 | 2 | 150 | 0 | 0.47 | 38350 | 1 | 1 | 0.956 | 0.876 | 0.751 | 0.658 | 0.565 | 0.402 | 0.182 | 0.04 | 0
| 37 | 141.9 | 2 | 2 | 1 | 30 | 0 | 0.47 | 39149 | 1 | 1 | 1 | 0.977 | 0.795 | 0.469 | 0.117 | 0.037 | 0.021 | 0.021 | 0
| 38 | 35 | 2 | 3 | 2 | 150 | 0 | 0.49 | 34248 | 1 | 1 | 1 | 1 | 0.896 | 0.456 | 0.137 | 0.035 | 0.02 | 0.02 | 0
| 39 | 23.8 | 2 | 5 | 2 | 150 | 0 | 0.56 | 34693 | 1 | 1 | 1 | 1 | 0.948 | 0.805 | 0.437 | 0.122 | 0.032 | 0.018 | 0
| 40 | 47.5 | 3 | 3 | 2 | 150 | 0 | 0.5 | 35143 | 1 | 1 | 1 | 0.994 | 0.887 | 0.542 | 0.176 | 0.05 | 0.02 | 0.02 | 0
| 41 | 24.8 | 0 | 6 | 2 | 150 | 0 | 0.65 | 40211 | 1 | 1 | 1 | 0.997 | 0.991 | 0.955 | 0.768 | 0.411 | 0.104 | 0.015 | 0
| 42 | 115.5 | 2 | 2 | 2 | 150 | 0 | 0.48 | 36003 | 1 | 1 | 0.993 | 0.953 | 0.798 | 0.578 | 0.296 | 0.097 | 0.037 | 0.021 | 0
| 43 | 372.8 | 3 | 2 | 1 | 30 | 0 | 0.42 | 36330 | 1 | 1 | 1 | 0.923 | 0.641 | 0.198 | 0.071 | 0.041 | 0.024 | 0.024 | 0
| 44 | 162 | 1 | 2 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 45 | 162 | 1 | 1 | 1 | 30 | 0 | 0.47 | 37364 | 1 | 1 | 0.99 | 0.935 | 0.82 | 0.649 | 0.259 | 0.084 | 0.038 | 0.021 | 0
| 46 | 7.9 | 0 | 2 | 2 | 150 | 0 | 0.57 | 35223 | 1 | 1 | 1 | 1 | 0.942 | 0.776 | 0.476 | 0.149 | 0.046 | 0.018 | 0
| 47 | 10.2 | 0 | 2 | 2 | 150 | 0 | 0.79 | 33961 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.983 | 0.909 | 0.595 | 0.058 | 0
| 48 | 104.1 | 1 | 6 | 2 | 150 | 0 | 0.61 | 36865 | 1 | 1 | 1 | 0.997 | 0.985 | 0.888 | 0.609 | 0.252 | 0.07 | 0.016 | 0
| 49 | 4.1 | 1 | 3 | 2 | 150 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.994 | 0.867 | 0.551 | 0.319 | 0.156 | 0.068 | 0.019 | 0
| 50 | 26.5 | 2 | 2 | 2 | 150 | 0 | 0.54 | 37147 | 1 | 1 | 1 | 0.979 | 0.824 | 0.66 | 0.498 | 0.306 | 0.127 | 0.035 | 0
| 51 | 6.7 | 0 | 1 | 2 | 150 | 0 | 0.49 | 38350 | 1 | 1 | 1 | 0.995 | 0.858 | 0.541 | 0.19 | 0.035 | 0.02 | 0.02 | 0
| 52 | 41.1 | 2 | 3 | 2 | 150 | 0 | 0.5 | 38401 | 1 | 1 | 1 | 0.973 | 0.835 | 0.647 | 0.29 | 0.077 | 0.02 | 0.02 | 0
| 53 | 20.7 | 0 | 1 | 2 | 150 | 0 | 0.48 | 34311 | 1 | 1 | 1 | 0.966 | 0.849 | 0.498 | 0.263 | 0.13 | 0.054 | 0.021 | 0
| 54 | 113.2 | 1 | 2 | 2 | 150 | 0 | 0.41 | 35530 | 1 | 1 | 0.996 | 0.887 | 0.615 | 0.346 | 0.137 | 0.06 | 0.024 | 0.024 | 0
| 55 | 122 | 2 | 2 | 2 | 150 | 0 | 0.44 | 35530 | 1 | 1 | 0.997 | 0.978 | 0.687 | 0.309 | 0.128 | 0.056 | 0.022 | 0.022 | 0
| 56 | 1.9 | 2 | 1 | 2 | 150 | 0 | 0.18 | 39965 | 1 | 0.806 | 0.71 | 0.604 | 0.416 | 0.27 | 0.211 | 0.178 | 0.097 | 0.054 | 0
| 57 | 4.5 | 0 | 1 | 2 | 150 | 0 | 0.44 | 29314 | 1 | 1 | 1 | 0.911 | 0.677 | 0.438 | 0.256 | 0.125 | 0.059 | 0.022 | 0
| 58 | 35.6 | 2 | 2 | 2 | 150 | 0 | 0.53 | 34661 | 1 | 1 | 1 | 0.995 | 0.927 | 0.655 | 0.308 | 0.116 | 0.034 | 0.019 | 0
| 59 | 227.3 | 2 | 2 | 2 | 150 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.996 | 0.931 | 0.46 | 0.19 | 0.165 | 0.12 | 0.037 | 0
| 60 | 5.7 | 2 | 2 | 2 | 150 | 0 | 0.49 | 33775 | 1 | 1 | 1 | 0.966 | 0.846 | 0.54 | 0.197 | 0.066 | 0.02 | 0.02 | 0
| 61 | 44 | 2 | 3 | 2 | 150 | 0 | 0.56 | 36084 | 1 | 1 | 1 | 1 | 0.973 | 0.715 | 0.415 | 0.165 | 0.047 | 0.018 | 0
| 62 | 424.7 | 3 | 6 | 2 | 150 | 0 | 0.33 | 39507 | 1 | 0.998 | 0.938 | 0.71 | 0.369 | 0.133 | 0.069 | 0.051 | 0.03 | 0.03 | 0
| 63 | 143.6 | 3 | 2 | 2 | 150 | 0 | 0.74 | 34366 | 1 | 1 | 1 | 0.996 | 0.958 | 0.941 | 0.918 | 0.857 | 0.451 | 0.187 | 0
| 64 | 48.6 | 3 | 5 | 2 | 150 | 0 | 0.54 | 34366 | 1 | 1 | 1 | 0.989 | 0.898 | 0.689 | 0.368 | 0.19 | 0.08 | 0.018 | 0
| 65 | 57.6 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34973 | 1 | 1 | 1 | 0.996 | 0.934 | 0.77 | 0.521 | 0.243 | 0.09 | 0.017 | 0
| 66 | 29.2 | 0 | 3 | 2 | 150 | 0 | 0.83 | 6050 | 1 | 1 | 1 | 1 | 0.991 | 0.975 | 0.956 | 0.941 | 0.823 | 0.432 | 0
| 67 | 25.4 | 2 | 3 | 2 | 150 | 0 | 0.46 | 34215 | 1 | 1 | 1 | 0.965 | 0.755 | 0.389 | 0.165 | 0.055 | 0.039 | 0.022 | 0
| 68 | 54.9 | 3 | 3 | 2 | 150 | 0 | 0.53 | 35051 | 1 | 1 | 1 | 0.994 | 0.905 | 0.699 | 0.256 | 0.075 | 0.019 | 0.019 | 0
| 69 | 63.2 | 2 | 1 | 2 | 150 | 0 | 0.52 | 32756 | 1 | 1 | 1 | 0.973 | 0.857 | 0.626 | 0.373 | 0.164 | 0.051 | 0.019 | 0
| 70 | 7 | 0 | 2 | 2 | 150 | 0 | 0.52 | 33951 | 1 | 1 | 1 | 0.995 | 0.905 | 0.664 | 0.284 | 0.104 | 0.034 | 0.019 | 0
| 71 | 264.3 | 2 | 2 | 2 | 150 | 0 | 0.37 | 36346 | 1 | 1 | 0.995 | 0.846 | 0.387 | 0.116 | 0.044 | 0.027 | 0.027 | 0.027 | 0
| 72 | 280 | 3 | 2 | 0 | 15 | 1 | 0.48 | 90000 | 1 | 1 | 1 | 0.976 | 0.766 | 0.505 | 0.27 | 0.15 | 0.073 | 0.021 | 0
| 73 | 10 | 0 | 1 | 2 | 150 | 0 | 0.31 | 44549 | 1 | 0.991 | 0.862 | 0.624 | 0.453 | 0.265 | 0.142 | 0.08 | 0.032 | 0.032 | 0
| 74 | 34 | 0 | 3 | 2 | 150 | 0 | 0.37 | 32960 | 1 | 1 | 1 | 0.88 | 0.331 | 0.085 | 0.043 | 0.027 | 0.027 | 0.027 | 0
| 75 | 532.9 | 4 | 2 | 1 | 30 | 0 | 0.52 | 36952 | 1 | 1 | 1 | 0.978 | 0.845 | 0.682 | 0.377 | 0.147 | 0.05 | 0.019 | 0
| 76 | 835 | 5 | 6 | 0 | 15 | 0 | 0.52 | 90000 | 1 | 1 | 1 | 0.978 | 0.837 | 0.639 | 0.407 | 0.148 | 0.051 | 0.019 | 0
| 77 | 1032.6 | 6 | 6 | 0 | 15 | 0 | 0.53 | 90000 | 1 | 1 | 1 | 1 | 0.892 | 0.67 | 0.317 | 0.089 | 0.034 | 0.019 | 0
| 78 | 1107.4 | 5 | 9 | 1 | 30 | 0 | 0.46 | 38534 | 1 | 1 | 1 | 0.959 | 0.766 | 0.406 | 0.135 | 0.038 | 0.022 | 0.022 | 0
| 79 | 101.4 | 2 | 2 | 2 | 150 | 0 | 0.52 | 36250 | 1 | 1 | 1 | 0.995 | 0.918 | 0.602 | 0.249 | 0.077 | 0.035 | 0.019 | 0
| 80 | 24 | 2 | 3 | 2 | 150 | 0 | 0.47 | 34906 | 1 | 1 | 1 | 0.976 | 0.81 | 0.4 | 0.147 | 0.037 | 0.021 | 0.021 | 0
| 81 | 47 | 2 | 3 | 2 | 150 | 0 | 0.53 | 34906 | 1 | 1 | 1 | 0.985 | 0.883 | 0.686 | 0.346 | 0.117 | 0.034 | 0.019 | 0
| 82 | 4.9 | 2 | 2 | 2 | 150 | 0 | 0.57 | 33891 | 1 | 1 | 1 | 1 | 0.949 | 0.753 | 0.514 | 0.215 | 0.061 | 0.017 | 0
| 83 | 209.7 | 3 | 4 | 2 | 150 | 0 | 0.97 | 39507 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 84 | 965.3 | 4 | 4 | 2 | 150 | 0 | 0.97 | 6050 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0
| 85 | 182.4 | 2 | 2 | 2 | 150 | 0 | 0.43 | 35530 | 1 | 1 | 0.993 | 0.909 | 0.7 | 0.379 | 0.13 | 0.057 | 0.023 | 0.023 | 0
| 86 | 32.2 | 2 | 2 | 2 | 150 | 0 | 0.59 | 33997 | 1 | 1 | 1 | 0.991 | 0.955 | 0.825 | 0.583 | 0.256 | 0.044 | 0.017 | 0
| 87 | 98.9 | 2 | 4 | 2 | 150 | 0 | 0.37 | 35530 | 1 | 1 | 0.933 | 0.851 | 0.594 | 0.362 | 0.172 | 0.067 | 0.027 | 0.027 | 0
| 88 | 473.8 | 3 | 2 | 2 | 150 | 0 | 0.32 | 35546 | 1 | 1 | 0.956 | 0.641 | 0.262 | 0.088 | 0.054 | 0.054 | 0.031 | 0.031 | 0
| 89 | 72.5 | 3 | 4 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 90 | 54.2 | 0 | 2 | 2 | 150 | 0 | 0.73 | 34842 | 1 | 1 | 1 | 0.989 | 0.962 | 0.95 | 0.943 | 0.915 | 0.265 | 0.026 | 0
| 91 | 20.4 | 1 | 3 | 2 | 150 | 0 | 0.38 | 34842 | 1 | 1 | 0.995 | 0.812 | 0.444 | 0.283 | 0.184 | 0.083 | 0.026 | 0.026 | 0
| 92 | 79.4 | 2 | 4 | 2 | 150 | 0 | 0.35 | 34085 | 1 | 1 | 0.973 | 0.774 | 0.337 | 0.11 | 0.048 | 0.029 | 0.029 | 0.029 | 0
| 93 | 3.5 | 2 | 4 | 2 | 150 | 0 | 0.47 | 34085 | 1 | 1 | 1 | 0.983 | 0.817 | 0.421 | 0.156 | 0.036 | 0.021 | 0.021 | 0
| 94 | 204.3 | 2 | 2 | 2 | 150 | 0 | 0.38 | 39507 | 1 | 0.998 | 0.941 | 0.825 | 0.491 | 0.375 | 0.259 | 0.125 | 0.048 | 0.026 | 0
| 95 | 164.1 | 2 | 2 | 2 | 150 | 0 | 0.57 | 34747 | 1 | 1 | 1 | 1 | 0.988 | 0.811 | 0.403 | 0.147 | 0.032 | 0.017 | 0
| 96 | 9.8 | 0 | 1 | 2 | 150 | 0 | 0.15 | 34747 | 1 | 0.994 | 0.994 | 0.994 | 0.751 | 0.214 | 0.067 | 0.067 | 0.067 | 0.067 | 0
| 97 | 180 | 2 | 4 | 2 | 150 | 0 | 0.55 | 37279 | 1 | 1 | 1 | 0.995 | 0.894 | 0.706 | 0.446 | 0.214 | 0.079 | 0.018 | 0
| 98 | 37.6 | 2 | 4 | 2 | 150 | 0 | 0.53 | 35914 | 1 | 1 | 1 | 0.995 | 0.941 | 0.675 | 0.276 | 0.074 | 0.019 | 0.019 | 0
| 99 | 13 | 0 | 2 | 2 | 150 | 0 | 0.34 | 32581 | 1 | 0.972 | 0.912 | 0.826 | 0.715 | 0.651 | 0.573 | 0.48 | 0.372 | 0.249 | 0
| 100 | 12 | 2 | 6 | 2 | 150 | 0 | 0.51 | 32581 | 1 | 1 | 1 | 0.994 | 0.868 | 0.537 | 0.316 | 0.153 | 0.052 | 0.019 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 111.55 | 36118.62 | 0 | 3 | N-1 | 20.07 | 20.69 | N2 | 20.7823 | 0.69847 | N1 | 20.0702 | 20.6949 | N | 20.8919 | 49.968 | 0 | 0 | 0 | 0 | 0.3 | 0
| 2 | 100 | 6050 | 0 | 3 | N-1 | 19 | 6.59 | N2 | 19.0108 | 6.5904 | N1 | 18.9981 | 6.593 | N | 21.1384 | 613.0674 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.76 | 34827.32 | 2 | 4 | N-1 | 6.63 | 5.36 | N2 | 7.0087 | 0.41721 | N1 | 6.627 | 5.3625 | N | 7.4966 | 39.0871 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 4 | 3.56 | 33792.6 | 1 | 1 | N-0 | 3.24 | 11.35 | N2 | 3.6955 | 1.0303 | N1 | 3.3247 | 11.3505 | N | 3.2406 | 11.3505 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 361.62 | 90000 | 3 | 1 | N-1 | 82.13 | 5.64 | N2 | 84.0384 | 0.5367 | N1 | 82.1304 | 5.638 | N | 96.95 | 332.2442 | 0 | 0 | 0 | 0 | 0.1 | 0
| 6 | 67.17 | 34024.46 | 2 | 2 | N-1 | 13.45 | 10.67 | N2 | 13.8073 | 2.0877 | N1 | 13.4496 | 10.6702 | N | 18.8257 | 197.4535 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 22.17 | 33835.17 | 0 | 2 | N-1 | 5.21 | 3.43 | N2 | 5.3537 | 0.74876 | N1 | 5.21 | 3.4257 | N | 6.7511 | 61.5252 | 0 | 0 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-0 | 2.25 | 23.29 | N2 | 2.4044 | 2.9978 | N1 | 2.252 | 23.2903 | N | 2.2519 | 23.2903 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 3.79 | 27.6 | N2 | 4.0147 | 5.6209 | N1 | 3.7879 | 27.5951 | N | 3.7904 | 43.6692 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 10 | 10 | 39506.97 | 2 | 2 | N-1 | 2.94 | 0.85 | N2 | 2.9672 | 0.85392 | N1 | 2.9415 | 0.85434 | N | 5.3199 | 70.5775 | 0 | 0.1 | 0 | 0 | 0 | 0
| 11 | 38 | 34429.94 | 2 | 1 | N-1 | 23.9 | 11.85 | N2 | 25.3706 | 1.6117 | N1 | 23.9017 | 11.846 | N | 24.3928 | 128.9274 | 0 | 0 | 0 | 0 | 0.3 | 0
| 12 | 22 | 34429.94 | 0 | 1 | N-1 | 15.6 | 1.19 | N2 | 15.8969 | 2.4 | N1 | 15.6019 | 1.1914 | N | 16.3638 | 114.3731 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 435 | 37279.21 | 4 | 5 | N-1 | 69.65 | 4.94 | N2 | 70.5329 | 4.0565 | N1 | 69.6456 | 4.9378 | N | 79.2607 | 353.5021 | 0 | 0.1 | 0 | 0 | 0 | 0
| 14 | 26.99 | 35252.82 | 0 | 1 | N-1 | 5.96 | 3.44 | N2 | 6.2824 | 0.6753 | N1 | 5.9616 | 3.4388 | N | 6.5717 | 47.103 | 0 | 0 | 0 | 0 | 0.3 | 0
| 15 | 47.75 | 36373.37 | 3 | 6 | N-1 | 11.46 | 1.45 | N2 | 11.9347 | 1.143 | N1 | 11.4631 | 1.4543 | N | 11.5784 | 17.9048 | 0 | 0.2 | 0 | 0 | 0 | 0
| 16 | 10.68 | 38166.21 | 0 | 2 | N-1 | 2.75 | 3.35 | N2 | 2.9193 | 1.0409 | N1 | 2.7533 | 3.3518 | N | 2.8685 | 8.2264 | 0 | 0 | 0 | 0 | 0.4 | 0
| 17 | 13 | 34357.34 | 3 | 3 | N-1 | 3.68 | 2.56 | N2 | 3.7312 | 1.3065 | N1 | 3.68 | 2.5577 | N | 4.0545 | 20.21 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 18 | 17.25 | 34357.34 | 3 | 3 | N-0 | 4.3 | 1.87 | N2 | 4.6124 | 0.25637 | N1 | 4.3005 | 1.8693 | N | 4.3004 | 1.8693 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 40 | 34357.34 | 0 | 2 | N-1 | 8.39 | 3.75 | N2 | 8.6835 | 1.1486 | N1 | 8.3908 | 3.7453 | N | 10.8587 | 94.3764 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30.16 | 33830.95 | 2 | 3 | N-1 | 6.88 | 4.17 | N2 | 7.5523 | 0.76504 | N1 | 6.8755 | 4.1672 | N | 6.8801 | 6.1629 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 21 | 571.03 | 39574.74 | 4 | 3 | N-1 | 83.28 | 18.5 | N2 | 83.3082 | 18.4931 | N1 | 83.2809 | 18.5001 | N | 144.4371 | 1723.0759 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 17.56 | 37690.78 | 2 | 1 | N-1 | 4.56 | 0.59 | N2 | 4.6546 | 1.3797 | N1 | 4.558 | 0.58712 | N | 5.8331 | 59.1824 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 45.05 | 35546.67 | 2 | 2 | N-1 | 9.68 | 6.98 | N2 | 9.9458 | 1.4173 | N1 | 9.6814 | 6.985 | N | 12.8713 | 117.1216 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 1.96 | 34513.16 | 0 | 1 | N-1 | 0.72 | 0.83 | N2 | 0.76575 | 1.0014 | N1 | 0.72415 | 0.83304 | N | 0.72423 | 4.2311 | 0 | 0 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 4.79 | 3 | N2 | 4.9215 | 0.60933 | N1 | 4.791 | 2.9986 | N | 6.0639 | 50.0656 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 17.67 | 35460.24 | 2 | 2 | N-1 | 4.54 | 3.67 | N2 | 4.6385 | 0.38384 | N1 | 4.5375 | 3.6667 | N | 5.1565 | 31.7154 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 30.77 | 34721.47 | 2 | 2 | N-1 | 7.08 | 4.77 | N2 | 7.2821 | 0.93808 | N1 | 7.0756 | 4.771 | N | 9.0519 | 77.5201 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 60 | 6050 | 2 | 2 | N-1 | 12.2 | 90.21 | N2 | 12.5295 | 2.9632 | N1 | 12.2 | 90.2109 | N | 12.5113 | 244.907 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 29 | 8 | 34432.4 | 2 | 3 | N-1 | 2.45 | 3.5 | N2 | 2.5872 | 1.2452 | N1 | 2.4521 | 3.504 | N | 2.6075 | 10.3845 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 80.03 | 36683.18 | 3 | 2 | N-1 | 15.37 | 15.16 | N2 | 15.8887 | 1.2726 | N1 | 15.37 | 15.1624 | N | 17.892 | 105.0419 | 0 | 0.2 | 0 | 0 | 0.3 | 0
| 31 | 25.06 | 36353.07 | 2 | 2 | N-1 | 5.99 | 3.87 | N2 | 6.1604 | 0.68975 | N1 | 5.9884 | 3.8736 | N | 7.4438 | 56.997 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8.41 | 32848.83 | 0 | 2 | N-1 | 2.16 | 1.84 | N2 | 2.3736 | 0.24519 | N1 | 2.159 | 1.8424 | N | 2.2313 | 10.8151 | 0 | 0 | 0 | 0 | 0.5 | 0
| 33 | 446.01 | 90000 | 3 | 1 | N-1 | 97.21 | 23.43 | N2 | 99.9096 | 0.30895 | N1 | 97.2126 | 23.4343 | N | 109.9359 | 335.5287 | 0 | 0 | 0 | 0 | 0.2 | 0
| 34 | 8.46 | 38350 | 0 | 1 | N-1 | 2.33 | 2.06 | N2 | 2.4595 | 0.26409 | N1 | 2.3283 | 2.0573 | N | 2.4807 | 15.4837 | 0 | 0 | 0 | 0 | 0.3 | 0
| 35 | 313.13 | 40649.71 | 2 | 4 | N-1 | 148.1 | 57.28 | N2 | 173.1179 | 1.0828 | N1 | 148.0951 | 57.2802 | N | 148.2866 | 67.664 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 36 | 8 | 38350 | 0 | 1 | N-1 | 2.29 | 2.11 | N2 | 2.3462 | 1.1177 | N1 | 2.2876 | 2.1133 | N | 2.3079 | 13.2034 | 0 | 0 | 0 | 0 | 0.1 | 0
| 37 | 141.89 | 39149.41 | 2 | 2 | N-1 | 8.21 | 4.55 | N2 | 8.5435 | 0.60246 | N1 | 8.2084 | 4.5481 | N | 9.5768 | 51.9745 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 38 | 35.04 | 34247.59 | 2 | 3 | N-1 | 7.92 | 8.66 | N2 | 8.5749 | 1.7351 | N1 | 7.9162 | 8.6578 | N | 8.0456 | 14.485 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 39 | 23.76 | 34693 | 2 | 5 | N-1 | 6.28 | 8.07 | N2 | 6.7552 | 1.1034 | N1 | 6.2792 | 8.0671 | N | 6.3151 | 10.5275 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 40 | 47.51 | 35142.51 | 3 | 3 | N-1 | 10.32 | 6.33 | N2 | 10.6596 | 0.33551 | N1 | 10.3224 | 6.3276 | N | 10.576 | 23.8144 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 24.79 | 40211.29 | 0 | 6 | N-1 | 6.49 | 0.29 | N2 | 6.4951 | 0.2877 | N1 | 6.4852 | 0.28796 | N | 7.1715 | 25.6013 | 0 | 0 | 0 | 0 | 0 | 0
| 42 | 115.5 | 36003.25 | 2 | 2 | N-1 | 21.06 | 17.23 | N2 | 21.5353 | 2.4682 | N1 | 21.0603 | 17.2288 | N | 27.3547 | 233.451 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 43 | 372.81 | 36329.98 | 3 | 2 | N-1 | 17.86 | 18.86 | N2 | 18.715 | 0.8618 | N1 | 17.8646 | 18.8598 | N | 18.3828 | 46.0638 | 0 | 0.3 | 0 | 0 | 0.4 | 0
| 44 | 162 | 37364.49 | 1 | 2 | N-2 | 9.51 | 0.96 | N2 | 9.5091 | 0.95816 | N1 | 9.5905 | 14.3023 | N | 11.3042 | 79.5468 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 162 | 37364.49 | 1 | 1 | N-1 | 9.18 | 5.89 | N2 | 9.5091 | 0.95816 | N1 | 9.1823 | 5.8942 | N | 9.941 | 63.5878 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 46 | 7.92 | 35222.85 | 0 | 2 | N-1 | 2.28 | 1.69 | N2 | 2.3327 | 0.29539 | N1 | 2.2815 | 1.6928 | N | 2.8527 | 24.2723 | 0 | 0 | 0 | 0 | 0.2 | 0
| 47 | 10.2 | 33960.97 | 0 | 2 | N-1 | 2.86 | 0.69 | N2 | 2.8671 | 0.68598 | N1 | 2.8571 | 0.68633 | N | 4.3757 | 56.3727 | 0 | 0 | 0 | 0 | 0 | 0
| 48 | 104.07 | 36864.7 | 1 | 6 | N-1 | 21.97 | 9.26 | N2 | 23.4906 | 0.95152 | N1 | 21.9717 | 9.2616 | N | 23.6093 | 79.021 | 0 | 0.9 | 0 | 0 | 0 | 0
| 49 | 4.09 | 32176.46 | 1 | 3 | N-1 | 1.41 | 2.17 | N2 | 1.4991 | 0.59335 | N1 | 1.4149 | 2.1674 | N | 1.4525 | 4.884 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 26.48 | 37146.71 | 2 | 2 | N-1 | 6.41 | 0.82 | N2 | 6.4473 | 0.8243 | N1 | 6.4055 | 0.8247 | N | 8.1517 | 68.1184 | 0 | 0.1 | 0 | 0 | 0 | 0
| 51 | 6.66 | 38350 | 0 | 1 | N-1 | 1.89 | 1.77 | N2 | 2.0161 | 1.5594 | N1 | 1.8913 | 1.7704 | N | 1.9864 | 11.3671 | 0 | 0 | 0 | 0 | 0.3 | 0
| 52 | 41.09 | 38401.47 | 2 | 3 | N-1 | 9.19 | 5.85 | N2 | 9.7988 | 0.43613 | N1 | 9.1944 | 5.851 | N | 9.9853 | 35.8672 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 20.68 | 34311.06 | 0 | 1 | N-1 | 4.87 | 4.84 | N2 | 5.0507 | 0.42251 | N1 | 4.8662 | 4.839 | N | 5.1315 | 34.713 | 0 | 0 | 0 | 0 | 0.3 | 0
| 54 | 113.15 | 35530.24 | 1 | 2 | N-1 | 20.53 | 26.59 | N2 | 21.1248 | 1.4126 | N1 | 20.5285 | 26.5934 | N | 22.7991 | 118.5846 | 0 | 0.9 | 0 | 0 | 0.3 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 21.7 | 22.89 | N2 | 22.4754 | 1.461 | N1 | 21.7038 | 22.8869 | N | 24.1154 | 120.6742 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 56 | 1.94 | 39964.51 | 2 | 1 | N-0 | 0.66 | 1.27 | N2 | 0.77466 | 0.10523 | N1 | 0.6767 | 1.0556 | N | 0.66299 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0
| 57 | 4.46 | 29313.64 | 0 | 1 | N-0 | 1.32 | 6.87 | N2 | 1.4339 | 0.76487 | N1 | 1.3545 | 6.8747 | N | 1.3195 | 6.8747 | 0 | 0 | 0 | 0 | 0 | 0
| 58 | 35.59 | 34661.38 | 2 | 2 | N-1 | 7.97 | 5.5 | N2 | 8.1998 | 1.0842 | N1 | 7.971 | 5.5017 | N | 10.2757 | 89.5966 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 227.28 | 40211.29 | 2 | 2 | N-1 | 37.46 | 4.07 | N2 | 37.6496 | 4.0714 | N1 | 37.4607 | 4.0722 | N | 48.6724 | 385.0798 | 0 | 0.1 | 0 | 0 | 0 | 0
| 60 | 5.7 | 33775.2 | 2 | 2 | N-1 | 1.77 | 2.5 | N2 | 1.86 | 1.3437 | N1 | 1.7736 | 2.4993 | N | 1.9704 | 10.8753 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 61 | 44.01 | 36084.4 | 2 | 3 | N-1 | 9.93 | 6.1 | N2 | 10.3781 | 0.75361 | N1 | 9.9347 | 6.0966 | N | 11.6097 | 69.2747 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 62 | 424.67 | 39506.97 | 3 | 6 | N-1 | 69.57 | 2.71 | N2 | 72.3422 | 0.99624 | N1 | 69.5737 | 2.7119 | N | 70.2694 | 92.4604 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 143.63 | 34366.43 | 3 | 2 | N-1 | 25.89 | 7.74 | N2 | 25.9099 | 7.7353 | N1 | 25.8936 | 7.7367 | N | 48.0611 | 736.2725 | 0 | 0 | 0 | 0 | 0 | 0
| 64 | 48.56 | 34366.43 | 3 | 5 | N-1 | 11.4 | 1.06 | N2 | 11.7742 | 0.46723 | N1 | 11.4013 | 1.0615 | N | 12.1181 | 39.4962 | 0 | 0.2 | 0 | 0 | 0 | 0
| 65 | 57.64 | 34973.02 | 2 | 2 | N-1 | 12.02 | 6.01 | N2 | 12.1843 | 1.9525 | N1 | 12.0168 | 6.0093 | N | 17.1283 | 184.6689 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 66 | 29.15 | 6050 | 0 | 3 | N-1 | 6.87 | 3.35 | N2 | 6.8817 | 3.3477 | N1 | 6.8712 | 3.3507 | N | 7.7187 | 240.6593 | 0 | 0 | 0 | 0 | 0 | 0
| 67 | 25.38 | 34214.81 | 2 | 3 | N-1 | 6.13 | 8.29 | N2 | 6.5849 | 1.4824 | N1 | 6.1285 | 8.2898 | N | 6.2159 | 12.4713 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 68 | 54.9 | 35050.92 | 3 | 3 | N-1 | 11.64 | 6.39 | N2 | 12.0068 | 0.60106 | N1 | 11.637 | 6.3925 | N | 12.47 | 42.7287 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 63.23 | 32755.83 | 2 | 1 | N-1 | 12.65 | 7.18 | N2 | 13.1196 | 1.7985 | N1 | 12.6545 | 7.1819 | N | 14.2455 | 119.458 | 0 | 0 | 0 | 0 | 0.2 | 0
| 70 | 7 | 33951.07 | 0 | 2 | N-1 | 2.04 | 1.89 | N2 | 2.1054 | 1.0924 | N1 | 2.0417 | 1.8918 | N | 2.3845 | 17.0392 | 0 | 0 | 0 | 0 | 0.2 | 0
| 71 | 264.3 | 36345.95 | 2 | 2 | N-1 | 39.77 | 31.58 | N2 | 42.4699 | 1.4226 | N1 | 39.7687 | 31.5849 | N | 40.5946 | 82.1605 | 0 | 0.5 | 0 | 0 | 0.4 | 0
| 72 | 280.03 | 90000 | 3 | 2 | N-1 | 67.29 | 8.57 | N2 | 68.0213 | 0.19398 | N1 | 67.2874 | 8.5716 | N | 79.809 | 212.9358 | 0 | 0 | 0 | 0 | 0.1 | 0
| 73 | 10 | 44548.95 | 0 | 1 | N-1 | 2.61 | 3.8 | N2 | 2.7607 | 0.71637 | N1 | 2.6065 | 3.8003 | N | 2.6386 | 10.6592 | 0 | 0 | 0 | 0 | 0.5 | 0
| 74 | 34 | 32960.09 | 0 | 3 | N-0 | 7.26 | 4.28 | N2 | 7.7322 | 0.61406 | N1 | 7.2559 | 4.2811 | N | 7.2559 | 4.2811 | 0 | 0 | 0 | 0 | 0 | 0
| 75 | 532.91 | 36951.61 | 4 | 2 | N-1 | 24.99 | 22.27 | N2 | 25.2924 | 3.1938 | N1 | 24.9876 | 22.2734 | N | 32.8765 | 280.1073 | 0 | 0 | 0 | 0 | 0.2 | 0
| 76 | 834.97 | 90000 | 5 | 6 | N-1 | 29.64 | 0.86 | N2 | 29.6431 | 0.85741 | N1 | 29.6426 | 0.85754 | N | 32.8601 | 51.3688 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 1032.64 | 90000 | 6 | 6 | N-1 | 35.11 | 0.85 | N2 | 35.1765 | 0.85006 | N1 | 35.1124 | 0.85021 | N | 37.9142 | 45.885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 78 | 1107.36 | 38534.2 | 5 | 9 | N-1 | 53.08 | 7.56 | N2 | 53.8003 | 1.1185 | N1 | 53.0797 | 7.5573 | N | 54.2125 | 76.5061 | 0 | 0.1 | 0 | 0 | 0 | 0
| 79 | 101.44 | 36249.54 | 2 | 2 | N-1 | 18.93 | 15.51 | N2 | 19.3613 | 2.4242 | N1 | 18.9298 | 15.514 | N | 25.3325 | 229.282 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 80 | 24 | 34906.04 | 2 | 3 | N-1 | 5.79 | 5.92 | N2 | 6.2808 | 1.202 | N1 | 5.7888 | 5.9183 | N | 5.8747 | 9.9085 | 0 | 0.5 | 0 | 0 | 0.3 | 0
| 81 | 47 | 34906.04 | 2 | 3 | N-1 | 10.41 | 11.27 | N2 | 10.9438 | 0.68442 | N1 | 10.4065 | 11.2735 | N | 11.5442 | 55.1908 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 82 | 4.89 | 33891.4 | 2 | 2 | N-1 | 1.63 | 2.95 | N2 | 1.6685 | 1.8897 | N1 | 1.6279 | 2.9473 | N | 1.9351 | 15.2973 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 209.66 | 39506.97 | 3 | 4 | N-1 | 39.08 | 32.5 | N2 | 39.0937 | 32.4807 | N1 | 39.0798 | 32.4984 | N | 150.5065 | 2929.5851 | 0 | 0 | 0 | 0 | 0 | 0
| 84 | 965.33 | 6050.12 | 4 | 4 | N-1 | 131.92 | 155.19 | N2 | 132.2602 | 155.1076 | N1 | 131.9163 | 155.1895 | N | 205.7743 | 13616.0885 | 0 | 0.1 | 0 | 0 | 0 | 0
| 85 | 182.39 | 35530.24 | 2 | 2 | N-1 | 30.33 | 34.38 | N2 | 31.3356 | 2.6094 | N1 | 30.3326 | 34.3799 | N | 35.3173 | 215.5592 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 86 | 32.16 | 33997.2 | 2 | 2 | N-1 | 7.41 | 7.21 | N2 | 7.5618 | 1.3712 | N1 | 7.4085 | 7.2129 | N | 10.4487 | 113.3242 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 87 | 98.91 | 35530.24 | 2 | 4 | N-1 | 19.49 | 17.75 | N2 | 21.0728 | 0.30116 | N1 | 19.4948 | 17.7462 | N | 19.6069 | 27.6312 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 88 | 473.81 | 35546.44 | 3 | 2 | N-0 | 64.56 | 96.7 | N2 | 68.6979 | 1.6818 | N1 | 64.5624 | 96.7024 | N | 64.5623 | 96.7024 | 0 | 0 | 0 | 0 | 0 | 0
| 89 | 72.49 | 34841.54 | 3 | 4 | N-1 | 15.07 | 12.36 | N2 | 15.7666 | 1.4217 | N1 | 15.0667 | 12.3577 | N | 15.2342 | 22.5424 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 54.2 | 34841.54 | 0 | 2 | N-1 | 11.2 | 2.76 | N2 | 11.2084 | 2.7591 | N1 | 11.1963 | 2.7596 | N | 18.8841 | 260.6887 | 0 | 0 | 0 | 0 | 0 | 0
| 91 | 20.38 | 34841.54 | 1 | 3 | N-1 | 5.12 | 4.09 | N2 | 5.5003 | 1.2593 | N1 | 5.1181 | 4.0889 | N | 5.1784 | 10.5879 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 79.39 | 34084.58 | 2 | 4 | N-0 | 15.93 | 11.88 | N2 | 17.549 | 1.4548 | N1 | 15.9347 | 11.8764 | N | 15.9346 | 11.8764 | 0 | 0 | 0 | 0 | 0 | 0
| 93 | 3.49 | 34084.58 | 2 | 4 | N-0 | 1.23 | 0.85 | N2 | 1.3643 | 0.10098 | N1 | 1.2298 | 0.84687 | N | 1.2297 | 0.84687 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | 204.31 | 39506.97 | 2 | 2 | N-1 | 33.86 | 28.76 | N2 | 34.4132 | 2.55 | N1 | 33.8647 | 28.7586 | N | 38.7064 | 210.6526 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 95 | 164.13 | 34746.88 | 2 | 2 | N-1 | 28.25 | 27.06 | N2 | 28.8539 | 5.8401 | N1 | 28.2526 | 27.0563 | N | 44.5376 | 552.3665 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 96 | 9.75 | 34746.88 | 0 | 1 | N-0 | 2.29 | 4.99 | N2 | 2.6816 | 0.2836 | N1 | 2.3517 | 4.9655 | N | 2.2927 | 4.9908 | 0 | 0 | 0 | 0 | 0 | 0
| 97 | 180 | 37279.21 | 2 | 4 | N-1 | 32.79 | 6.18 | N2 | 34.603 | 2.3893 | N1 | 32.786 | 6.1822 | N | 38.8929 | 223.1559 | 0 | 0.3 | 0 | 0 | 0 | 0
| 98 | 37.57 | 35914.09 | 2 | 4 | N-1 | 8.8 | 8.86 | N2 | 9.5097 | 1.0064 | N1 | 8.8022 | 8.8597 | N | 8.9709 | 16.6658 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 99 | 13 | 32580.51 | 0 | 2 | N-1 | 3.45 | 1.3 | N2 | 3.4588 | 1.2977 | N1 | 3.4486 | 1.2984 | N | 3.664 | 20.2412 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 11.96 | 32580.51 | 2 | 6 | N-1 | 3.66 | 1.07 | N2 | 3.9623 | 0.71611 | N1 | 3.6648 | 1.072 | N | 3.6887 | 6.2109 | 0 | 0.4 | 0 | 0 | 0 | 0

## DR
|  | $ millions | MWhr
ID | Connection Point | total cost | total EUE | study #
1 | Albury 132 kV | 6.179 | 4.1977 | 7607 | N-1
2 | ANM 132 kV | 5.5564 | 24.997 | 6621 | N-1
3 | Armidale 66 kV | 3.8046 | 1.592 | 17208 | N-1
4 | Balranald 22 kV | 1.7606 | 2.4698 | 6501 | N-1
5 | Beaconsfield 132 kV | 18.3934 | 6.5465 | 8583 | N-1
6 | Beryl 66 kV | 3.7375 | 2.6123 | 7601 | N-1
7 | Boambee South 132 kV | 1.831 | 0.84396 | 7601 | N-1
8 | Boggabri East | 0.94076 | 2.632 | 6615 | N-1
9 | Boggabri North | 1.4001 | 4.9351 | 6615 | N-1
10 | Brandy Hill 132 kV | 1.1628 | 1.118 | 7600 | N-1
11 | Broken Hill 22 kV | 6.5153 | 1.5527 | 7667 | N-1
12 | Broken Hill 220 kV | 5.6395 | 49.266 | 9365 | N-1
13 | Canberra 132 kV Note 3 | 18.1226 | 8.0808 | 9263 | N-1
14 | Casino 132 kV | 1.8801 | 0.64878 | 7601 | N-1
15 | Coffs Harbour 66 kV | 4.3777 | 2.6914 | 17208 | N-1
16 | Coleambally 132 kV | 1.3714 | 1.4534 | 7600 | N-1
17 | Cooma 11 kV | 1.4604 | 1.0618 | 7605 | N-1
18 | Cooma 66 kV | 1.9866 | 1.7152 | 7605 | N-1
19 | Cooma 132 kV | 3.2998 | 6.1492 | 6486 | N-1
20 | Cowra 66 kV | 2.4953 | 3.197 | 7581 | N-1
21 | Dapto 132 kV | 18.7277 | 9.1755 | 8609 | N-1
22 | Darlington Point 132 kV Note 3 | 1.9278 | 1.9205 | 7557 | N-1
23 | Deniliquin 66 kV | 3.0696 | 1.9291 | 7601 | N-1
24 | Dorrigo 132 kV | 0.53073 | 0.85493 | 7245 | N-1
25 | Finley 132 kV | 1.8072 | 2.4597 | 6486 | N-1
26 | Finley 66 kV | 1.7783 | 0.80378 | 7601 | N-1
27 | Forbes 66 kV | 2.424 | 1.3262 | 7601 | N-1
28 | Gadara (132 kV & 11 kV) | 3.7765 | 17.479 | 6616 | N-1
29 | Glen Innes 66 kV | 1.38 | 1.2788 | 7581 | N-1
30 | Griffith 33 kV | 4.5675 | 2.9845 | 7649 | N-1
31 | Gunnedah 66 kV | 2.0924 | 1.0449 | 7601 | N-1
32 | Hawks Nest 132 kV | 0.86657 | 1.3308 | 7359 | N-1
33 | Haymarket 132 kV | 21.0081 | 8.041 | 8583 | N-1
34 | Herons Creek | 1.1647 | 1.6166 | 7486 | N-1
35 | Holroyd 132 kV | 40.0607 | 17.9376 | 8541 | N-1
36 | Ilford 132 kV | 0.74282 | 1.4249 | 7245 | N-1
37 | Ingleburn 66 kV | 2.6577 | 1.8801 | 7601 | N-1
38 | Inverell 66 kV | 2.8129 | 2.8819 | 7582 | N-1
39 | Kempsey 33 kV | 2.6424 | 2.2038 | 17184 | N-1
40 | Koolkhan 66 kV | 3.3375 | 2.6198 | 7606 | N-1
41 | Liddell 330 kV (33 kV supply via Mac Gen) | 3.3063 | 2.0474 | 17208 | N-1
42 | Lismore 132 kV Note 3 | 5.9969 | 4.264 | 8542 | N-1
43 | Liverpool 132 kV | 5.2664 | 2.8851 | 7649 | N-1
44 | Macarthur 132 kV | 4.4971 | 1.9759 | 8825 | N-1
45 | Macarthur 66 kV | 2.7672 | 0.43366 | 8837 | N-1
46 | Macksville 132 kV | 1.0807 | 1.7796 | 7599 | N-1
47 | Manildra 132 kV | 1.1652 | 1.118 | 7600 | N-1
48 | Marulan 132 kV | 8.291 | 7.2336 | 17226 | N-1
49 | Molong 66 kV | 0.78326 | 0.6913 | 7461 | N-1
50 | Moree 66 kV | 2.6948 | 1.5674 | 7601 | N-1
51 | Morven 132 kV | 0.87331 | 1.3308 | 7359 | N-1
52 | Mount Piper 66 kV | 3.1164 | 3.3622 | 7582 | N-1
53 | Mudgee 132 kV | 1.6562 | 0.52864 | 7601 | N-1
54 | Munmorah 132 kV | 5.7812 | 11.1424 | 7487 | N-1
55 | Munmorah 330 kV (via old Power Stn Txs) | 5.561 | 4.903 | 7601 | N-1
56 | Munyang 33 kV | 2.9779 | 3.1221 | 7582 | N-1
57 | Murrumbateman 132 kV | 0.71623 | 0.9981 | 7359 | N-1
58 | Murrumburrah 66 kV | 2.735 | 1.6076 | 7601 | N-1
59 | Muswellbrook 132 kV | 8.8102 | 9.8864 | 7601 | N-1
60 | Nambucca 66 kV | 1.0781 | 1.7796 | 7599 | N-1
61 | Narrabri 66 kV | 3.5319 | 0.91398 | 8567 | N-1
62 | Newcastle 132 kV | 18.3731 | 0.99829 | 9311 | N-1
63 | Orange North 132 kV | 7.3366 | 7.208 | 9365 | N-1
64 | Orange 66 kV | 3.2362 | 1.2765 | 7667 | N-1
65 | Panorama 66 kV | 4.0434 | 2.974 | 7601 | N-1
66 | Parkes 132 kV | 2.5431 | 4.0585 | 6486 | N-1
67 | Parkes 66 kV | 2.242 | 2.6642 | 7581 | N-1
68 | Port Macquarie 33 kV | 4.1408 | 2.2524 | 7607 | N-1
69 | Queanbeyan 66 kV | 4.2638 | 3.9991 | 7583 | N-1
70 | Raleigh 132 kV | 1.1543 | 1.9773 | 7599 | N-1
71 | Regentville 132 kV | 9.6136 | 11.3734 | 7601 | N-1
72 | Rookwood Road 132 kV | 16.221 | 5.3888 | 8583 | N-1
73 | Snowy Adit 132 kV | 1.1747 | 1.6166 | 7486 | N-1
74 | Stroud 132 kV | 2.285 | 1.2057 | 7601 | N-1
75 | Sydney East 132 kV | 8.4911 | 2.459 | 8627 | N-1
76 | Sydney North 132 kV | 10.8745 | 1.085 | 8865 | N-1
77 | Sydney South 132 kV | 11.2698 | 1.1822 | 8865 | N-1
78 | Sydney West 132 kV | 16.0918 | 7.5954 | 9063 | N-1
79 | Tamworth 66 kV | 5.4711 | 3.968 | 7649 | N-1
80 | Taree 33 kV | 2.1601 | 2.5576 | 7581 | N-1
81 | Taree 66 kV | 3.4307 | 3.9226 | 7582 | N-1
82 | Tenterfield 22 kV | 0.83446 | 1.1864 | 7599 | N-1
83 | Tomago 132 Note 3 | 8.1667 | 32.4598 | 6665 | N-1
84 | Tomago 330 kV | 24.3187 | 49.93 | 7624 | N-1
85 | Tuggerah 132 kV | 7.683 | 8.0779 | 7601 | N-1
86 | Tumut 66 kV | 2.6521 | 1.5272 | 7601 | N-1
87 | Vales Pt 132 kV | 5.2584 | 4.2778 | 8541 | N-1
88 | Vineyard 132 kV | 13.9898 | 16.8556 | 7649 | N-1
89 | Wagga 66 kV | 5.2744 | 3.2763 | 7607 | N-1
90 | Wagga North 132 kV | 3.8042 | 2.27 | 7446 | N-1
91 | Wagga North 66 kV | 2.3501 | 3.733 | 7461 | N-1
92 | Wallerawang 132 kV Note 3 | 6.2661 | 4.551 | 8542 | N-1
93 | Wallerawang 66 kV | 2.2879 | 1.2057 | 7601 | N-1
94 | Waratah West 132 kV | 6.5428 | 6.2694 | 7601 | N-1
95 | Wellington 132 kV Note 3 | 7.5947 | 3.2553 | 7446 | N-1
96 | Wellington Town | 1.1392 | 0.96416 | 7600 | N-1
97 | Williamsdale 132 kV Note 3 | 8.7411 | 2.5851 | 8567 | N-1
98 | Yanco 33 kV | 3.1249 | 1.9124 | 8541 | N-1
99 | Yass 132 kV | 1.3615 | 1.5988 | 6486 | N-1
100 | Yass 66 kV | 1.3638 | 2.1015 | 7486 | N-1
101 | test
Notes:
1. The greater of the forecast connected customer loads in summer 2015/16 and winter 2016.
2. Based on the capacity of TransGrid’s (or the customer’s) transformers or, where there are no transformers, the capacity of the customer’s lines (or TransGrid’s switchbays connecting those lines). Note that the capability of TransGrid’s network may limit supply to groups of connection points (such as those serving a particular area). Those limitations cannot meaningfully be included in the individual connection point capabilities.
3. This 330/132 kV substation also supplies TransGrid 132 kV lines, the loadings on which are not included in the forecast.

## out23_0
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 45
oh_line_life_in_yrs | 80
ug_cable_life_in_yrs | 80
discount_rate | 0.059
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.0048243
failures_per_annum_per_100km_oh_line | 0.35
failures_per_annum_per_100km_ug_cable | 0.15
coef_for_transformer_cost_function_coef*MVA^exp | 0.0942
exponent_for_transformer_cost_function | 0.6404
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6404
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 6570
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 168 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 2190 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 4380 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 123 | 3 | 3 | 2 | 75 | 0 | 0.51 | 38258 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 2 | 110 | 3 | 3 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 3 | 38 | 2 | 8 | 2 | 75 | 0 | 0.51 | 35161 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 4 | 4 | 1 | 2 | 3 | 150 | 0 | 0.51 | 33793 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 5 | 311 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 6 | 65 | 2 | 2 | 2 | 75 | 0 | 0.51 | 43661 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 7 | 21 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33835 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 8 | 8 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 9 | 15 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 10 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 11 | 38 | 2 | 1 | 3 | 150 | 0 | 0.51 | 41904 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 12 | 23 | 0 | 1 | 3 | 150 | 0 | 0.51 | 41904 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 13 | 478 | 2 | 6 | 2 | 75 | 0 | 0.51 | 37279 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 14 | 27 | 1 | 1 | 2 | 75 | 0 | 0.51 | 37266 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 15 | 54 | 2 | 6 | 2 | 75 | 0 | 0.51 | 36373 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 16 | 13 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40836 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 17 | 13 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 18 | 21 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 19 | 50 | 0 | 2 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 20 | 30 | 2 | 3 | 2 | 75 | 0 | 0.51 | 34206 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 21 | 677 | 4 | 3 | 2 | 75 | 0 | 0.51 | 39575 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 22 | 18 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38717 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 23 | 48 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36866 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 24 | 3 | 1 | 2 | 2 | 75 | 0 | 0.51 | 34513 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 25 | 20 | 0 | 2 | 2 | 75 | 0 | 0.51 | 35460 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 26 | 20 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35460 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 27 | 33 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35267 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 28 | 70 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 29 | 12 | 2 | 3 | 2 | 75 | 0 | 0.51 | 34432 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 30 | 88 | 3 | 2 | 2 | 75 | 0 | 0.51 | 39334 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 31 | 26 | 2 | 2 | 2 | 75 | 0 | 0.51 | 37391 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 32 | 8 | 1 | 1 | 2 | 75 | 0 | 0.51 | 33288 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 33 | 382 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 34 | 10 | 1 | 2 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 35 | 402 | 2 | 4 | 1 | 15 | 1 | 0.51 | 40650 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 36 | 5 | 1 | 2 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 37 | 135 | 2 | 2 | 1 | 15 | 0 | 0.51 | 39149 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 38 | 36 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 39 | 27 | 2 | 5 | 2 | 75 | 0 | 0.51 | 35258 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 40 | 47 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35438 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 41 | 38 | 2 | 5 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 42 | 104 | 2 | 4 | 2 | 75 | 0 | 0.51 | 35974 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 43 | 377 | 3 | 2 | 1 | 15 | 0 | 0.51 | 36330 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 44 | 298 | 1 | 2 | 1 | 15 | 0 | 0.51 | 37364 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 45 | 178 | 1 | 1 | 1 | 15 | 0 | 0.51 | 37364 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 46 | 9 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35223 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 47 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 42392 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 48 | 144 | 1 | 6 | 2 | 75 | 0 | 0.51 | 36865 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 49 | 5 | 1 | 3 | 2 | 75 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 50 | 39 | 2 | 2 | 2 | 75 | 0 | 0.51 | 37695 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 51 | 8 | 1 | 1 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 52 | 42 | 2 | 3 | 2 | 75 | 0 | 0.51 | 38401 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 53 | 22 | 1 | 1 | 2 | 75 | 0 | 0.51 | 34311 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 54 | 122 | 1 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 55 | 122 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 56 | 39 | 2 | 3 | 2 | 75 | 0 | 0.51 | 40708 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 57 | 6 | 1 | 1 | 2 | 75 | 0 | 0.51 | 29314 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 58 | 40 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35796 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 59 | 246 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 60 | 9 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33775 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 61 | 51 | 2 | 3 | 2 | 75 | 0 | 0.51 | 39211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 62 | 462 | 3 | 7 | 2 | 75 | 0 | 0.51 | 39507 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 63 | 153 | 0 | 5 | 2 | 75 | 0 | 0.51 | 44830 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 64 | 62 | 2 | 1 | 2 | 75 | 0 | 0.51 | 44830 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 65 | 74 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38006 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 66 | 33 | 0 | 1 | 2 | 75 | 0 | 0.51 | 43962 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 67 | 25 | 2 | 3 | 2 | 75 | 0 | 0.51 | 43962 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 68 | 66 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35178 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 69 | 69 | 2 | 3 | 2 | 75 | 0 | 0.51 | 33238 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 70 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33951 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 71 | 283 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36346 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 72 | 256 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 73 | 10 | 1 | 2 | 2 | 75 | 0 | 0.51 | 44549 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 74 | 30 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35892 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 75 | 692 | 4 | 3 | 1 | 15 | 0 | 0.51 | 41374 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 76 | 917 | 5 | 7 | 0 | 8 | 0 | 0.51 | 34631 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 77 | 930 | 6 | 7 | 0 | 8 | 0 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 78 | 1263 | 5 | 10 | 1 | 15 | 0 | 0.51 | 38534 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 79 | 117 | 3 | 2 | 2 | 75 | 0 | 0.51 | 36520 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 80 | 24 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35038 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 81 | 49 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35038 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 82 | 6 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36309 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 83 | 229 | 3 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 84 | 940 | 6 | 4 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 85 | 201 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 86 | 38 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38210 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 87 | 85 | 2 | 4 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 88 | 497 | 3 | 2 | 2 | 75 | 0 | 0.51 | 35546 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 89 | 96 | 3 | 3 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 90 | 60 | 0 | 4 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 91 | 27 | 1 | 3 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 92 | 111 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38306 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 93 | 30 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38306 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 94 | 156 | 2 | 2 | 2 | 75 | 0 | 0.51 | 39507 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 95 | 174 | 0 | 2 | 2 | 75 | 0 | 0.51 | 39924 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 96 | 12 | 1 | 1 | 2 | 75 | 0 | 0.51 | 39924 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 97 | 186 | 2 | 4 | 2 | 75 | 0 | 0.51 | 37279 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 98 | 38 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38289 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 99 | 13 | 0 | 2 | 2 | 75 | 0 | 0.51 | 32601 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 100 | 13 | 1 | 2 | 2 | 75 | 0 | 0.51 | 32601 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE
| 1 | 123 | 38257.78 | 3 | 3 | N-1 | 6.18 | 4.2 | N2 | 6.3178 | 1.01 | N1 | 6.179 | 4.1984 | N | 7.9221 | 56.7267
| 2 | 110 | 6050 | 3 | 3 | N-1 | 5.56 | 25.01 | N2 | 5.8105 | 6.8459 | N1 | 5.5564 | 25.0066 | N | 5.6605 | 50.7312
| 3 | 38 | 35160.52 | 2 | 8 | N-1 | 3.8 | 1.59 | N2 | 4.0872 | 0.01536 | N1 | 3.8046 | 1.592 | N | 3.8277 | 4.2073
| 4 | 4 | 33792.6 | 1 | 2 | N-1 | 1.76 | 2.47 | N2 | 1.8743 | 1.4219 | N1 | 1.7607 | 2.4703 | N | 1.9686 | 11.2252
| 5 | 311 | 38808.21 | 3 | 4 | N-1 | 18.39 | 6.55 | N2 | 20.359 | 1.5433 | N1 | 18.3934 | 6.547 | N | 19.5348 | 47.3238
| 6 | 65 | 43661.5 | 2 | 2 | N-1 | 3.74 | 2.61 | N2 | 3.8525 | 1.0414 | N1 | 3.7375 | 2.6124 | N | 7.4348 | 94.0333
| 7 | 21 | 33835.17 | 2 | 2 | N-1 | 1.83 | 0.84 | N2 | 1.9021 | 0.42312 | N1 | 1.831 | 0.84402 | N | 2.6442 | 30.38
| 8 | 8 | 6050 | 2 | 2 | N-1 | 0.94 | 2.63 | N2 | 0.99677 | 1.4747 | N1 | 0.94076 | 2.6323 | N | 0.94794 | 11.5733
| 9 | 15 | 6050 | 2 | 2 | N-1 | 1.4 | 4.94 | N2 | 1.4825 | 2.7651 | N1 | 1.4001 | 4.9356 | N | 1.4366 | 21.7
| 10 | 10 | 40211.29 | 2 | 2 | N-1 | 1.16 | 1.12 | N2 | 1.2062 | 0.92751 | N1 | 1.1628 | 1.1181 | N | 1.592 | 14.4667
| 11 | 38 | 41903.58 | 2 | 1 | N-1 | 6.52 | 1.55 | N2 | 7.6811 | 1.476 | N1 | 6.5153 | 1.5527 | N | 8.8606 | 84.2684
| 12 | 23 | 41903.58 | 0 | 1 | N-1 | 4.43 | 0.93 | N2 | 5.2618 | 0.79184 | N1 | 4.4299 | 0.93246 | N | 5.6394 | 49.266
| 13 | 478 | 37279.21 | 2 | 6 | N-1 | 18.12 | 8.08 | N2 | 19.1323 | 0.38596 | N1 | 18.1226 | 8.0811 | N | 19.1675 | 56.7208
| 14 | 27 | 37265.94 | 1 | 1 | N-1 | 1.88 | 0.65 | N2 | 2.2216 | 0.54402 | N1 | 1.8801 | 0.64878 | N | 2.6491 | 30.5113
| 15 | 54 | 36373.37 | 2 | 6 | N-1 | 4.38 | 2.69 | N2 | 4.7299 | 0.73165 | N1 | 4.3777 | 2.6914 | N | 4.4252 | 6.4078
| 16 | 13 | 40835.88 | 2 | 2 | N-1 | 1.37 | 1.45 | N2 | 1.422 | 1.2058 | N1 | 1.3714 | 1.4536 | N | 1.9602 | 18.8067
| 17 | 13 | 35389.13 | 3 | 3 | N-1 | 1.46 | 1.06 | N2 | 1.5136 | 0.76941 | N1 | 1.4604 | 1.0627 | N | 1.5827 | 5.9955
| 18 | 21 | 35389.13 | 3 | 3 | N-1 | 1.99 | 1.72 | N2 | 2.0564 | 1.2429 | N1 | 1.9867 | 1.7166 | N | 2.2003 | 9.685
| 19 | 50 | 35389.13 | 0 | 2 | N-1 | 2.81 | 1.64 | N2 | 2.896 | 0.78673 | N1 | 2.8072 | 1.6386 | N | 4.9128 | 68.5538
| 20 | 30 | 34206.04 | 2 | 3 | N-1 | 2.5 | 3.2 | N2 | 2.6473 | 1.9249 | N1 | 2.4954 | 3.1991 | N | 2.8293 | 15.3814
| 21 | 677 | 39574.74 | 4 | 3 | N-1 | 18.73 | 9.18 | N2 | 18.8899 | 3.908 | N1 | 18.7278 | 9.1777 | N | 29.3402 | 301.2242
| 22 | 18 | 38717.16 | 2 | 4 | N-1 | 1.93 | 1.92 | N2 | 2.0681 | 0.48168 | N1 | 1.9279 | 1.9221 | N | 1.9754 | 3.9281
| 23 | 48 | 36865.92 | 2 | 2 | N-1 | 3.07 | 1.93 | N2 | 3.1777 | 0.96714 | N1 | 3.0696 | 1.9292 | N | 5.3005 | 69.44
| 24 | 3 | 34513.16 | 1 | 2 | N-1 | 0.53 | 0.86 | N2 | 0.55728 | 0.53962 | N1 | 0.53074 | 0.85522 | N | 0.61612 | 4.2904
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 1.59 | 0.66 | N2 | 1.6447 | 0.31469 | N1 | 1.5925 | 0.65546 | N | 2.3622 | 27.4215
| 26 | 20 | 35460.24 | 2 | 2 | N-1 | 1.78 | 0.8 | N2 | 1.8469 | 0.40297 | N1 | 1.7783 | 0.80383 | N | 2.5928 | 28.9333
| 27 | 33 | 35266.87 | 2 | 2 | N-1 | 2.42 | 1.33 | N2 | 2.5142 | 0.66491 | N1 | 2.424 | 1.3263 | N | 3.8398 | 47.74
| 28 | 70 | 6050 | 2 | 2 | N-1 | 3.78 | 17.48 | N2 | 3.9712 | 6.8038 | N1 | 3.7765 | 17.4801 | N | 4.1042 | 101.2667
| 29 | 12 | 34432.4 | 2 | 3 | N-1 | 1.38 | 1.28 | N2 | 1.4728 | 0.76996 | N1 | 1.38 | 1.2796 | N | 1.4983 | 6.1526
| 30 | 88 | 39333.93 | 3 | 2 | N-1 | 4.57 | 2.98 | N2 | 4.6925 | 1.4033 | N1 | 4.5675 | 2.9847 | N | 8.9246 | 122.7728
| 31 | 26 | 37390.97 | 2 | 2 | N-1 | 2.09 | 1.04 | N2 | 2.1705 | 0.52387 | N1 | 2.0924 | 1.045 | N | 3.2582 | 37.6133
| 32 | 8 | 33287.63 | 1 | 1 | N-1 | 0.87 | 1.33 | N2 | 1.0363 | 1.439 | N1 | 0.86657 | 1.3308 | N | 0.9984 | 9.0404
| 33 | 382 | 38808.21 | 3 | 4 | N-1 | 21.01 | 8.04 | N2 | 23.2279 | 1.8957 | N1 | 21.0081 | 8.0417 | N | 22.4653 | 58.1276
| 34 | 10 | 38350 | 1 | 2 | N-1 | 1.16 | 1.62 | N2 | 1.2045 | 0.92751 | N1 | 1.1647 | 1.6167 | N | 1.5411 | 14.3013
| 35 | 402 | 40649.71 | 2 | 4 | N-1 | 40.06 | 17.94 | N2 | 44.9954 | 3.632 | N1 | 40.0608 | 17.9397 | N | 43.401 | 134.382
| 36 | 5 | 38350 | 1 | 2 | N-1 | 0.74 | 1.43 | N2 | 0.77219 | 0.89937 | N1 | 0.74284 | 1.4254 | N | 0.9165 | 7.1506
| 37 | 135 | 39149.41 | 2 | 2 | N-1 | 2.66 | 1.88 | N2 | 2.7086 | 1.0127 | N1 | 2.6577 | 1.8801 | N | 4.2291 | 47.1686
| 38 | 36 | 35529.74 | 2 | 3 | N-1 | 2.81 | 2.88 | N2 | 2.9758 | 1.2502 | N1 | 2.8129 | 2.8831 | N | 3.2434 | 18.4577
| 39 | 27 | 35258.16 | 2 | 5 | N-1 | 2.64 | 2.2 | N2 | 2.8638 | 0.39036 | N1 | 2.6423 | 2.2038 | N | 2.6535 | 3.3129
| 40 | 47 | 35437.84 | 3 | 3 | N-1 | 3.34 | 2.62 | N2 | 3.4419 | 1.4749 | N1 | 3.3375 | 2.6214 | N | 3.8727 | 21.6761
| 41 | 38 | 40211.29 | 2 | 5 | N-1 | 3.31 | 2.05 | N2 | 3.5633 | 0.39251 | N1 | 3.3063 | 2.0474 | N | 3.3427 | 4.6626
| 42 | 104 | 35974 | 2 | 4 | N-1 | 6 | 4.27 | N2 | 6.346 | 1.6074 | N1 | 5.9969 | 4.2657 | N | 6.415 | 22.6956
| 43 | 377 | 36329.98 | 3 | 2 | N-1 | 5.27 | 2.89 | N2 | 5.3514 | 1.2439 | N1 | 5.2664 | 2.8851 | N | 8.927 | 112.299
| 44 | 298 | 37364.49 | 1 | 2 | N-2 | 4.45 | 2.24 | N2 | 4.4466 | 2.2355 | N1 | 4.4972 | 1.9759 | N | 7.677 | 99.1911
| 45 | 178 | 37364.49 | 1 | 1 | N-1 | 2.77 | 0.43 | N2 | 3.2149 | 1.3353 | N1 | 2.7671 | 0.43366 | N | 4.2668 | 48.6384
| 46 | 9 | 35222.85 | 2 | 2 | N-1 | 1.08 | 1.78 | N2 | 1.121 | 1.6189 | N1 | 1.0807 | 1.7799 | N | 1.404 | 13.02
| 47 | 10 | 42391.55 | 2 | 2 | N-1 | 1.17 | 1.12 | N2 | 1.2083 | 0.92751 | N1 | 1.1652 | 1.1181 | N | 1.6235 | 14.4667
| 48 | 144 | 36864.7 | 2 | 6 | N-1 | 8.29 | 7.23 | N2 | 8.8661 | 1.3566 | N1 | 8.291 | 7.2336 | N | 8.3638 | 14.7056
| 49 | 5 | 32176.46 | 1 | 3 | N-1 | 0.78 | 0.69 | N2 | 0.84651 | 0.32081 | N1 | 0.78327 | 0.69164 | N | 0.80966 | 2.4809
| 50 | 39 | 37694.51 | 2 | 2 | N-1 | 2.69 | 1.57 | N2 | 2.7914 | 0.7858 | N1 | 2.6949 | 1.5675 | N | 4.5259 | 56.42
| 51 | 8 | 38350 | 1 | 1 | N-1 | 0.87 | 1.33 | N2 | 1.0435 | 1.439 | N1 | 0.87331 | 1.3308 | N | 1.0442 | 9.0404
| 52 | 42 | 38401.47 | 2 | 3 | N-1 | 3.12 | 3.36 | N2 | 3.2859 | 1.4585 | N1 | 3.1165 | 3.3637 | N | 3.6826 | 21.534
| 53 | 22 | 34311.06 | 1 | 1 | N-1 | 1.66 | 0.53 | N2 | 1.9573 | 0.44327 | N1 | 1.6562 | 0.52864 | N | 2.1788 | 24.8611
| 54 | 122 | 35530.24 | 1 | 2 | N-2 | 5.73 | 2.46 | N2 | 5.7309 | 2.4581 | N1 | 5.7812 | 11.1427 | N | 11.1477 | 174.4754
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 5.56 | 4.9 | N2 | 5.7309 | 2.4581 | N1 | 5.561 | 4.9034 | N | 11.2647 | 176.4934
| 56 | 39 | 40708.41 | 2 | 3 | N-1 | 2.98 | 3.12 | N2 | 3.1375 | 1.1933 | N1 | 2.9779 | 3.1234 | N | 3.5375 | 19.9958
| 57 | 6 | 29313.64 | 1 | 1 | N-1 | 0.72 | 1 | N2 | 0.85771 | 1.0792 | N1 | 0.71623 | 0.9981 | N | 0.78125 | 6.7803
| 58 | 40 | 35796.16 | 2 | 2 | N-1 | 2.73 | 1.61 | N2 | 2.8344 | 0.80595 | N1 | 2.735 | 1.6077 | N | 4.5098 | 57.8667
| 59 | 246 | 40211.29 | 2 | 2 | N-1 | 8.81 | 9.89 | N2 | 9.0032 | 3.9412 | N1 | 8.8103 | 9.8871 | N | 22.1719 | 355.8801
| 60 | 9 | 33775.2 | 2 | 2 | N-1 | 1.08 | 1.78 | N2 | 1.1186 | 1.6189 | N1 | 1.0781 | 1.7799 | N | 1.3851 | 13.02
| 61 | 51 | 39210.77 | 2 | 3 | N-1 | 3.53 | 0.91 | N2 | 3.7126 | 0.30949 | N1 | 3.5319 | 0.91415 | N | 4.2589 | 26.1484
| 62 | 462 | 39506.97 | 3 | 7 | N-1 | 18.37 | 1 | N2 | 19.1067 | 1.4626 | N1 | 18.3731 | 0.99869 | N | 18.7921 | 29.1371
| 63 | 153 | 44829.77 | 0 | 5 | N-1 | 7.32 | 2.72 | N2 | 7.4078 | 0.95287 | N1 | 7.3179 | 2.7236 | N | 7.3366 | 7.208
| 64 | 62 | 44829.77 | 2 | 1 | N-1 | 3.24 | 1.28 | N2 | 3.7405 | 0.99331 | N1 | 3.2362 | 1.2765 | N | 5.8145 | 71.0886
| 65 | 74 | 38005.74 | 2 | 2 | N-1 | 4.04 | 2.97 | N2 | 4.1751 | 1.1856 | N1 | 4.0434 | 2.9742 | N | 7.6872 | 107.0534
| 66 | 33 | 43962.19 | 0 | 1 | N-1 | 1.91 | 0.67 | N2 | 2.2407 | 0.51924 | N1 | 1.9071 | 0.66894 | N | 3.0583 | 35.343
| 67 | 25 | 43962.19 | 2 | 3 | N-1 | 2.24 | 2.67 | N2 | 2.3698 | 1.5009 | N1 | 2.2421 | 2.6659 | N | 2.6138 | 12.8178
| 68 | 66 | 35178.34 | 3 | 3 | N-1 | 4.14 | 2.25 | N2 | 4.2616 | 0.54196 | N1 | 4.1408 | 2.2528 | N | 4.9287 | 30.4387
| 69 | 69 | 33237.78 | 2 | 3 | N-1 | 4.26 | 4 | N2 | 4.4847 | 0.70353 | N1 | 4.2638 | 3.9995 | N | 5.1012 | 35.3772
| 70 | 10 | 33951.07 | 2 | 2 | N-1 | 1.15 | 1.98 | N2 | 1.1977 | 1.7987 | N1 | 1.1543 | 1.9776 | N | 1.5014 | 14.4667
| 71 | 283 | 36345.95 | 2 | 2 | N-1 | 9.61 | 11.37 | N2 | 9.8378 | 4.534 | N1 | 9.6136 | 11.3742 | N | 23.49 | 409.4067
| 72 | 256 | 38808.21 | 3 | 4 | N-1 | 16.22 | 5.39 | N2 | 17.9713 | 1.2704 | N1 | 16.221 | 5.3892 | N | 17.1227 | 38.9547
| 73 | 10 | 44548.95 | 1 | 2 | N-1 | 1.17 | 1.62 | N2 | 1.2103 | 0.92751 | N1 | 1.1747 | 1.6167 | N | 1.6298 | 14.3013
| 74 | 30 | 35892.2 | 2 | 2 | N-1 | 2.29 | 1.21 | N2 | 2.3703 | 0.60446 | N1 | 2.285 | 1.2057 | N | 3.5865 | 43.4
| 75 | 692 | 41373.9 | 4 | 3 | N-1 | 8.49 | 2.46 | N2 | 8.5185 | 0.92851 | N1 | 8.4911 | 2.4591 | N | 10.7498 | 65.664
| 76 | 917 | 34631.49 | 5 | 7 | N-1 | 10.87 | 1.09 | N2 | 10.8749 | 1.085 | N1 | 10.8745 | 1.0854 | N | 10.9596 | 5.8692
| 77 | 930 | 38808.21 | 6 | 7 | N-1 | 11.27 | 1.18 | N2 | 11.2701 | 1.1822 | N1 | 11.2698 | 1.1828 | N | 11.3713 | 5.7565
| 78 | 1263 | 38534.2 | 5 | 10 | N-1 | 16.09 | 7.6 | N2 | 16.1621 | 1.7049 | N1 | 16.0919 | 7.5967 | N | 16.1502 | 10.0217
| 79 | 117 | 36519.99 | 3 | 2 | N-1 | 5.47 | 3.97 | N2 | 5.6188 | 1.8658 | N1 | 5.4711 | 3.9683 | N | 10.8798 | 163.232
| 80 | 24 | 35038.31 | 2 | 3 | N-1 | 2.16 | 2.56 | N2 | 2.2948 | 1.5399 | N1 | 2.1602 | 2.5593 | N | 2.4289 | 12.3051
| 81 | 49 | 35038.31 | 2 | 3 | N-1 | 3.43 | 3.92 | N2 | 3.6189 | 0.49961 | N1 | 3.4307 | 3.9243 | N | 4.0321 | 25.123
| 82 | 6 | 36309.05 | 2 | 2 | N-1 | 0.83 | 1.19 | N2 | 0.86526 | 1.0792 | N1 | 0.83447 | 1.1866 | N | 1.0483 | 8.68
| 83 | 229 | 6050.12 | 3 | 2 | N-1 | 8.17 | 32.46 | N2 | 8.5141 | 4.7548 | N1 | 8.1667 | 32.4604 | N | 9.517 | 319.4884
| 84 | 940 | 6050.12 | 6 | 4 | N-1 | 24.32 | 49.97 | N2 | 25.1657 | 20.0616 | N1 | 24.3189 | 49.9721 | N | 24.5882 | 149.5957
| 85 | 201 | 35530.24 | 2 | 2 | N-1 | 7.68 | 8.08 | N2 | 7.8892 | 4.0499 | N1 | 7.6831 | 8.0785 | N | 17.2281 | 290.7801
| 86 | 38 | 38209.75 | 2 | 2 | N-1 | 2.65 | 1.53 | N2 | 2.747 | 0.76565 | N1 | 2.6521 | 1.5273 | N | 4.4602 | 54.9733
| 87 | 85 | 35530.24 | 2 | 4 | N-1 | 5.26 | 4.28 | N2 | 5.5785 | 2.2746 | N1 | 5.2585 | 4.2806 | N | 5.577 | 18.5493
| 88 | 497 | 35546.44 | 3 | 2 | N-1 | 13.99 | 16.86 | N2 | 14.2283 | 7.9255 | N1 | 13.9899 | 16.8569 | N | 37.174 | 693.3874
| 89 | 96 | 39800.19 | 3 | 3 | N-1 | 5.27 | 3.28 | N2 | 5.401 | 0.53639 | N1 | 5.2744 | 3.2768 | N | 6.6677 | 44.2745
| 90 | 60 | 39800.19 | 0 | 4 | N-1 | 3.74 | 3.05 | N2 | 3.8323 | 1.1055 | N1 | 3.7376 | 3.0528 | N | 3.9047 | 8.5582
| 91 | 27 | 39800.19 | 1 | 3 | N-1 | 2.35 | 3.73 | N2 | 2.4835 | 1.7324 | N1 | 2.3501 | 3.7348 | N | 2.6581 | 13.3967
| 92 | 111 | 38306.25 | 2 | 4 | N-1 | 6.27 | 4.55 | N2 | 6.6188 | 1.2574 | N1 | 6.2662 | 4.5529 | N | 6.766 | 24.2232
| 93 | 30 | 38306.25 | 2 | 2 | N-1 | 2.29 | 1.21 | N2 | 2.3718 | 0.60446 | N1 | 2.2879 | 1.2057 | N | 3.6913 | 43.4
| 94 | 156 | 39506.97 | 2 | 2 | N-1 | 6.54 | 6.27 | N2 | 6.7162 | 2.4993 | N1 | 6.5429 | 6.2699 | N | 14.7693 | 225.68
| 95 | 174 | 39924.38 | 0 | 2 | N-1 | 6.24 | 5.7 | N2 | 6.3923 | 2.7378 | N1 | 6.2408 | 5.7025 | N | 15.0449 | 238.5674
| 96 | 12 | 39924.38 | 1 | 1 | N-1 | 1.14 | 0.96 | N2 | 1.3513 | 1.113 | N1 | 1.1392 | 0.96416 | N | 1.4423 | 13.5606
| 97 | 186 | 37279.21 | 2 | 4 | N-1 | 8.74 | 2.59 | N2 | 9.1905 | 0.35496 | N1 | 8.7411 | 2.5853 | N | 9.6533 | 40.5903
| 98 | 38 | 38289.45 | 2 | 4 | N-1 | 3.12 | 1.91 | N2 | 3.3313 | 1.0169 | N1 | 3.1249 | 1.9137 | N | 3.2535 | 8.2926
| 99 | 13 | 32600.58 | 0 | 2 | N-1 | 1.22 | 1.34 | N2 | 1.2597 | 1.1313 | N1 | 1.2189 | 1.3403 | N | 1.6401 | 17.824
| 100 | 13 | 32600.58 | 1 | 2 | N-1 | 1.36 | 2.1 | N2 | 1.4121 | 1.2058 | N1 | 1.3638 | 2.1018 | N | 1.7782 | 18.5916

## out25_input0
opex_capital_ratio | 0.02
transformer_cost_multiplier | 2.5
line_cost_multiplier | 1.1
transformer_life_in_yrs | 45
oh_line_life_in_yrs | 80
ug_cable_life_in_yrs | 80
discount_rate | 0.059
capital_efficiency_factor | 0.5
failures_per_transformer_per_annum | 0.0048243
failures_per_annum_per_100km_oh_line | 0.35
failures_per_annum_per_100km_ug_cable | 0.15
coef_for_transformer_cost_function_coef*MVA^exp | 0.0942
exponent_for_transformer_cost_function | 0.6404
coef_for_line_cost_function_coef*MVA^exp | 0.0248
exponent_for_line_cost_function | 0.6404
cost_multiplier_underground_cables | 15
max_hrs_to_replace/repair_transformer | 6570
max_hrs_to_repair_OH_line | 120
max_hrs_to_repair_cable | 2016
restor
| ID | fixcap | pmvacap | fixop | pmvaop | hr2restore
| 0 | 0 | 0 | 0 | 0 | 0
| 1 | 1 | 0.002 | 0 | 0 | 0.083
| 2 | 0.5 | 0.001 | 0 | 0 | 0.5
| 3 | 0.1 | 0.0002 | 0 | 0 | 1
| 4 | 0 | 0 | 0.05 | 0.0002 | 4
| 5 | 0 | 0 | 0.1 | 0.0004 | 8
tx | repair
| ID | hr2repair | fixcap | pmvacap | fixop | pmvaop | sfixcap | spmvacap | sop
| 1 | 24 | 0 | 0.0144 | 0.05 | 0.001 | 1.44 | 1.4388 | 0.15
| 2 | 168 | 0 | 0.0036 | 0.1 | 0.003 | 0.36 | 0.3597 | 0.4
| 3 | 2190 | 0 | 0 | 0 | 0.0018 | 0.18 | 0 | 0.18
| 4 | 4380 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ln | repair
| ID | ohhr2repair | fixcap | pmvacap | fixop | pmvaop | ughr2repair | fixcap | pmvacap | fixop | pmvaop
| 1 | 8 | 0.1 | 0.001 | 0.05 | 0.002 | 168 | 0.2 | 0.002 | 0.1 | 0.007
| 2 | 24 | 0 | 0 | 0.05 | 0.002 | 672 | 0 | 0.002 | 0.1 | 0.007
| 3 | 48 | 0 | 0 | 0.05 | 0.0015 | 1344 | 0 | 0 | 0.05 | 0.0025
| 4 | 120 | 0 | 0 | 0.05 | 0.0005 | 2016 | 0 | 0 | 0.05 | 0.001
load | type | multipliers
| ID | txcost | ohcost | ugcost | failrate | linelen
| 0 | 2 | 2 | 1 | 1 | 15
| 1 | 1.5 | 1.5 | 1 | 1 | 30
| 2 | 1 | 1 | 1 | 1 | 150
| 3 | 1.5 | 1.5 | 1 | 1 | 300
BSP | data
| bsp | maxdem | #tx | #ln | loc | length | ugflag | lf | vcr | MVA/ln | LDC | points | ...
| 1 | 123 | 3 | 3 | 2 | 75 | 0 | 0.51 | 38258 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 2 | 110 | 3 | 3 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 3 | 38 | 2 | 8 | 2 | 75 | 0 | 0.51 | 35161 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 4 | 4 | 1 | 2 | 3 | 150 | 0 | 0.51 | 33793 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 5 | 311 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 6 | 65 | 2 | 2 | 2 | 75 | 0 | 0.51 | 43661 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 7 | 21 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33835 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 8 | 8 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 9 | 15 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 10 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 11 | 38 | 2 | 1 | 3 | 150 | 0 | 0.51 | 41904 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 12 | 23 | 0 | 1 | 3 | 150 | 0 | 0.51 | 41904 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 13 | 478 | 2 | 6 | 2 | 75 | 0 | 0.51 | 37279 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 14 | 27 | 1 | 1 | 2 | 75 | 0 | 0.51 | 37266 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 15 | 54 | 2 | 6 | 2 | 75 | 0 | 0.51 | 36373 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 16 | 13 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40836 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 17 | 13 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 18 | 21 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 19 | 50 | 0 | 2 | 2 | 75 | 0 | 0.51 | 35389 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 20 | 30 | 2 | 3 | 2 | 75 | 0 | 0.51 | 34206 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 21 | 677 | 4 | 3 | 2 | 75 | 0 | 0.51 | 39575 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 22 | 18 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38717 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 23 | 48 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36866 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 24 | 3 | 1 | 2 | 2 | 75 | 0 | 0.51 | 34513 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 25 | 20 | 0 | 2 | 2 | 75 | 0 | 0.51 | 35460 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 26 | 20 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35460 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 27 | 33 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35267 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 28 | 70 | 2 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 29 | 12 | 2 | 3 | 2 | 75 | 0 | 0.51 | 34432 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 30 | 88 | 3 | 2 | 2 | 75 | 0 | 0.51 | 39334 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 31 | 26 | 2 | 2 | 2 | 75 | 0 | 0.51 | 37391 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 32 | 8 | 1 | 1 | 2 | 75 | 0 | 0.51 | 33288 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 33 | 382 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 34 | 10 | 1 | 2 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 35 | 402 | 2 | 4 | 1 | 15 | 1 | 0.51 | 40650 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 36 | 5 | 1 | 2 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 37 | 135 | 2 | 2 | 1 | 15 | 0 | 0.51 | 39149 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 38 | 36 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 39 | 27 | 2 | 5 | 2 | 75 | 0 | 0.51 | 35258 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 40 | 47 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35438 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 41 | 38 | 2 | 5 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 42 | 104 | 2 | 4 | 2 | 75 | 0 | 0.51 | 35974 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 43 | 377 | 3 | 2 | 1 | 15 | 0 | 0.51 | 36330 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 44 | 298 | 1 | 2 | 1 | 15 | 0 | 0.51 | 37364 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 45 | 178 | 1 | 1 | 1 | 15 | 0 | 0.51 | 37364 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 46 | 9 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35223 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 47 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 42392 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 48 | 144 | 1 | 6 | 2 | 75 | 0 | 0.51 | 36865 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 49 | 5 | 1 | 3 | 2 | 75 | 0 | 0.51 | 32176 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 50 | 39 | 2 | 2 | 2 | 75 | 0 | 0.51 | 37695 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 51 | 8 | 1 | 1 | 2 | 75 | 0 | 0.51 | 38350 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 52 | 42 | 2 | 3 | 2 | 75 | 0 | 0.51 | 38401 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 53 | 22 | 1 | 1 | 2 | 75 | 0 | 0.51 | 34311 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 54 | 122 | 1 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 55 | 122 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 56 | 39 | 2 | 3 | 2 | 75 | 0 | 0.51 | 40708 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 57 | 6 | 1 | 1 | 2 | 75 | 0 | 0.51 | 29314 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 58 | 40 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35796 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 59 | 246 | 2 | 2 | 2 | 75 | 0 | 0.51 | 40211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 60 | 9 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33775 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 61 | 51 | 2 | 3 | 2 | 75 | 0 | 0.51 | 39211 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 62 | 462 | 3 | 7 | 2 | 75 | 0 | 0.51 | 39507 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 63 | 153 | 0 | 5 | 2 | 75 | 0 | 0.51 | 44830 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 64 | 62 | 2 | 1 | 2 | 75 | 0 | 0.51 | 44830 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 65 | 74 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38006 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 66 | 33 | 0 | 1 | 2 | 75 | 0 | 0.51 | 43962 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 67 | 25 | 2 | 3 | 2 | 75 | 0 | 0.51 | 43962 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 68 | 66 | 3 | 3 | 2 | 75 | 0 | 0.51 | 35178 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 69 | 69 | 2 | 3 | 2 | 75 | 0 | 0.51 | 33238 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 70 | 10 | 2 | 2 | 2 | 75 | 0 | 0.51 | 33951 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 71 | 283 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36346 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 72 | 256 | 3 | 4 | 0 | 8 | 1 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 73 | 10 | 1 | 2 | 2 | 75 | 0 | 0.51 | 44549 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 74 | 30 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35892 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 75 | 692 | 4 | 3 | 1 | 15 | 0 | 0.51 | 41374 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 76 | 917 | 5 | 7 | 0 | 8 | 0 | 0.51 | 34631 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 77 | 930 | 6 | 7 | 0 | 8 | 0 | 0.51 | 38808 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 78 | 1263 | 5 | 10 | 1 | 15 | 0 | 0.51 | 38534 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 79 | 117 | 3 | 2 | 2 | 75 | 0 | 0.51 | 36520 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 80 | 24 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35038 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 81 | 49 | 2 | 3 | 2 | 75 | 0 | 0.51 | 35038 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 82 | 6 | 2 | 2 | 2 | 75 | 0 | 0.51 | 36309 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 83 | 229 | 3 | 2 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 84 | 940 | 6 | 4 | 2 | 75 | 0 | 0.51 | 6050 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 85 | 201 | 2 | 2 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 86 | 38 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38210 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 87 | 85 | 2 | 4 | 2 | 75 | 0 | 0.51 | 35530 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 88 | 497 | 3 | 2 | 2 | 75 | 0 | 0.51 | 35546 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 89 | 96 | 3 | 3 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 90 | 60 | 0 | 4 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 91 | 27 | 1 | 3 | 2 | 75 | 0 | 0.51 | 39800 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 92 | 111 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38306 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 93 | 30 | 2 | 2 | 2 | 75 | 0 | 0.51 | 38306 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 94 | 156 | 2 | 2 | 2 | 75 | 0 | 0.51 | 39507 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 95 | 174 | 0 | 2 | 2 | 75 | 0 | 0.51 | 39924 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 96 | 12 | 1 | 1 | 2 | 75 | 0 | 0.51 | 39924 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 97 | 186 | 2 | 4 | 2 | 75 | 0 | 0.51 | 37279 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 98 | 38 | 2 | 4 | 2 | 75 | 0 | 0.51 | 38289 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 99 | 13 | 0 | 2 | 2 | 75 | 0 | 0.51 | 32601 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| 100 | 13 | 1 | 2 | 2 | 75 | 0 | 0.51 | 32601 | 1 | 1 | 1 | 0.992 | 0.864 | 0.639 | 0.292 | 0.057 | 0.009 | 0.003 | 0
| bsp | max_demand | vcr | tx | ln | N-x | mincost | opt_EUE | N2 | cost | EUE | N1 | cost | EUE | N | cost | EUE | txlar2 | 1 | N | llar2 | 1 | N
| 1 | 123 | 38257.78 | 3 | 3 | N-1 | 6.18 | 4.2 | N2 | 6.3178 | 1.01 | N1 | 6.179 | 4.1984 | N | 7.9221 | 56.7267 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 2 | 110 | 6050 | 3 | 3 | N-1 | 5.56 | 25.01 | N2 | 5.8105 | 6.8459 | N1 | 5.5564 | 25.0066 | N | 5.6605 | 50.7312 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 3 | 38 | 35160.52 | 2 | 8 | N-1 | 3.8 | 1.59 | N2 | 4.0872 | 0.01536 | N1 | 3.8046 | 1.592 | N | 3.8277 | 4.2073 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 4 | 4 | 33792.6 | 1 | 2 | N-1 | 1.76 | 2.47 | N2 | 1.8743 | 1.4219 | N1 | 1.7607 | 2.4703 | N | 1.9686 | 11.2252 | 0 | 0.9 | 0 | 0 | 0.3 | 0
| 5 | 311 | 38808.21 | 3 | 4 | N-1 | 18.39 | 6.55 | N2 | 20.359 | 1.5433 | N1 | 18.3934 | 6.547 | N | 19.5348 | 47.3238 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 6 | 65 | 43661.5 | 2 | 2 | N-1 | 3.74 | 2.61 | N2 | 3.8525 | 1.0414 | N1 | 3.7375 | 2.6124 | N | 7.4348 | 94.0333 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 7 | 21 | 33835.17 | 2 | 2 | N-1 | 1.83 | 0.84 | N2 | 1.9021 | 0.42312 | N1 | 1.831 | 0.84402 | N | 2.6442 | 30.38 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 8 | 8 | 6050 | 2 | 2 | N-1 | 0.94 | 2.63 | N2 | 0.99677 | 1.4747 | N1 | 0.94076 | 2.6323 | N | 0.94794 | 11.5733 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 9 | 15 | 6050 | 2 | 2 | N-1 | 1.4 | 4.94 | N2 | 1.4825 | 2.7651 | N1 | 1.4001 | 4.9356 | N | 1.4366 | 21.7 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 10 | 10 | 40211.29 | 2 | 2 | N-1 | 1.16 | 1.12 | N2 | 1.2062 | 0.92751 | N1 | 1.1628 | 1.1181 | N | 1.592 | 14.4667 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 11 | 38 | 41903.58 | 2 | 1 | N-1 | 6.52 | 1.55 | N2 | 7.6811 | 1.476 | N1 | 6.5153 | 1.5527 | N | 8.8606 | 84.2684 | 0 | 0 | 0 | 0 | 0.2 | 0
| 12 | 23 | 41903.58 | 0 | 1 | N-1 | 4.43 | 0.93 | N2 | 5.2618 | 0.79184 | N1 | 4.4299 | 0.93246 | N | 5.6394 | 49.266 | 0 | 0 | 0 | 0 | 0.2 | 0
| 13 | 478 | 37279.21 | 2 | 6 | N-1 | 18.12 | 8.08 | N2 | 19.1323 | 0.38596 | N1 | 18.1226 | 8.0811 | N | 19.1675 | 56.7208 | 0 | 0.4 | 0 | 0 | 0 | 0
| 14 | 27 | 37265.94 | 1 | 1 | N-1 | 1.88 | 0.65 | N2 | 2.2216 | 0.54402 | N1 | 1.8801 | 0.64878 | N | 2.6491 | 30.5113 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 15 | 54 | 36373.37 | 2 | 6 | N-1 | 4.38 | 2.69 | N2 | 4.7299 | 0.73165 | N1 | 4.3777 | 2.6914 | N | 4.4252 | 6.4078 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 16 | 13 | 40835.88 | 2 | 2 | N-1 | 1.37 | 1.45 | N2 | 1.422 | 1.2058 | N1 | 1.3714 | 1.4536 | N | 1.9602 | 18.8067 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 17 | 13 | 35389.13 | 3 | 3 | N-1 | 1.46 | 1.06 | N2 | 1.5136 | 0.76941 | N1 | 1.4604 | 1.0627 | N | 1.5827 | 5.9955 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 18 | 21 | 35389.13 | 3 | 3 | N-1 | 1.99 | 1.72 | N2 | 2.0564 | 1.2429 | N1 | 1.9867 | 1.7166 | N | 2.2003 | 9.685 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 19 | 50 | 35389.13 | 0 | 2 | N-1 | 2.81 | 1.64 | N2 | 2.896 | 0.78673 | N1 | 2.8072 | 1.6386 | N | 4.9128 | 68.5538 | 0 | 0 | 0 | 0 | 0.2 | 0
| 20 | 30 | 34206.04 | 2 | 3 | N-1 | 2.5 | 3.2 | N2 | 2.6473 | 1.9249 | N1 | 2.4954 | 3.1991 | N | 2.8293 | 15.3814 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 21 | 677 | 39574.74 | 4 | 3 | N-1 | 18.73 | 9.18 | N2 | 18.8899 | 3.908 | N1 | 18.7278 | 9.1777 | N | 29.3402 | 301.2242 | 0 | 0.1 | 0 | 0 | 0.1 | 0
| 22 | 18 | 38717.16 | 2 | 4 | N-1 | 1.93 | 1.92 | N2 | 2.0681 | 0.48168 | N1 | 1.9279 | 1.9221 | N | 1.9754 | 3.9281 | 0 | 0.5 | 0 | 0 | 0.2 | 0
| 23 | 48 | 36865.92 | 2 | 2 | N-1 | 3.07 | 1.93 | N2 | 3.1777 | 0.96714 | N1 | 3.0696 | 1.9292 | N | 5.3005 | 69.44 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 24 | 3 | 34513.16 | 1 | 2 | N-1 | 0.53 | 0.86 | N2 | 0.55728 | 0.53962 | N1 | 0.53074 | 0.85522 | N | 0.61612 | 4.2904 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 25 | 20 | 35460.24 | 0 | 2 | N-1 | 1.59 | 0.66 | N2 | 1.6447 | 0.31469 | N1 | 1.5925 | 0.65546 | N | 2.3622 | 27.4215 | 0 | 0 | 0 | 0 | 0.2 | 0
| 26 | 20 | 35460.24 | 2 | 2 | N-1 | 1.78 | 0.8 | N2 | 1.8469 | 0.40297 | N1 | 1.7783 | 0.80383 | N | 2.5928 | 28.9333 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 27 | 33 | 35266.87 | 2 | 2 | N-1 | 2.42 | 1.33 | N2 | 2.5142 | 0.66491 | N1 | 2.424 | 1.3263 | N | 3.8398 | 47.74 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 28 | 70 | 6050 | 2 | 2 | N-1 | 3.78 | 17.48 | N2 | 3.9712 | 6.8038 | N1 | 3.7765 | 17.4801 | N | 4.1042 | 101.2667 | 0 | 0.4 | 0 | 0 | 0.3 | 0
| 29 | 12 | 34432.4 | 2 | 3 | N-1 | 1.38 | 1.28 | N2 | 1.4728 | 0.76996 | N1 | 1.38 | 1.2796 | N | 1.4983 | 6.1526 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 30 | 88 | 39333.93 | 3 | 2 | N-1 | 4.57 | 2.98 | N2 | 4.6925 | 1.4033 | N1 | 4.5675 | 2.9847 | N | 8.9246 | 122.7728 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 31 | 26 | 37390.97 | 2 | 2 | N-1 | 2.09 | 1.04 | N2 | 2.1705 | 0.52387 | N1 | 2.0924 | 1.045 | N | 3.2582 | 37.6133 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 32 | 8 | 33287.63 | 1 | 1 | N-1 | 0.87 | 1.33 | N2 | 1.0363 | 1.439 | N1 | 0.86657 | 1.3308 | N | 0.9984 | 9.0404 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 33 | 382 | 38808.21 | 3 | 4 | N-1 | 21.01 | 8.04 | N2 | 23.2279 | 1.8957 | N1 | 21.0081 | 8.0417 | N | 22.4653 | 58.1276 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 34 | 10 | 38350 | 1 | 2 | N-1 | 1.16 | 1.62 | N2 | 1.2045 | 0.92751 | N1 | 1.1647 | 1.6167 | N | 1.5411 | 14.3013 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 35 | 402 | 40649.71 | 2 | 4 | N-1 | 40.06 | 17.94 | N2 | 44.9954 | 3.632 | N1 | 40.0608 | 17.9397 | N | 43.401 | 134.382 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 36 | 5 | 38350 | 1 | 2 | N-1 | 0.74 | 1.43 | N2 | 0.77219 | 0.89937 | N1 | 0.74284 | 1.4254 | N | 0.9165 | 7.1506 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 37 | 135 | 39149.41 | 2 | 2 | N-1 | 2.66 | 1.88 | N2 | 2.7086 | 1.0127 | N1 | 2.6577 | 1.8801 | N | 4.2291 | 47.1686 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 38 | 36 | 35529.74 | 2 | 3 | N-1 | 2.81 | 2.88 | N2 | 2.9758 | 1.2502 | N1 | 2.8129 | 2.8831 | N | 3.2434 | 18.4577 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 39 | 27 | 35258.16 | 2 | 5 | N-1 | 2.64 | 2.2 | N2 | 2.8638 | 0.39036 | N1 | 2.6423 | 2.2038 | N | 2.6535 | 3.3129 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 40 | 47 | 35437.84 | 3 | 3 | N-1 | 3.34 | 2.62 | N2 | 3.4419 | 1.4749 | N1 | 3.3375 | 2.6214 | N | 3.8727 | 21.6761 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 41 | 38 | 40211.29 | 2 | 5 | N-1 | 3.31 | 2.05 | N2 | 3.5633 | 0.39251 | N1 | 3.3063 | 2.0474 | N | 3.3427 | 4.6626 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 42 | 104 | 35974 | 2 | 4 | N-1 | 6 | 4.27 | N2 | 6.346 | 1.6074 | N1 | 5.9969 | 4.2657 | N | 6.415 | 22.6956 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 43 | 377 | 36329.98 | 3 | 2 | N-1 | 5.27 | 2.89 | N2 | 5.3514 | 1.2439 | N1 | 5.2664 | 2.8851 | N | 8.927 | 112.299 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 44 | 298 | 37364.49 | 1 | 2 | N-2 | 4.45 | 2.24 | N2 | 4.4466 | 2.2355 | N1 | 4.4972 | 1.9759 | N | 7.677 | 99.1911 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 45 | 178 | 37364.49 | 1 | 1 | N-1 | 2.77 | 0.43 | N2 | 3.2149 | 1.3353 | N1 | 2.7671 | 0.43366 | N | 4.2668 | 48.6384 | 0 | 0.1 | 0 | 0 | 0 | 0
| 46 | 9 | 35222.85 | 2 | 2 | N-1 | 1.08 | 1.78 | N2 | 1.121 | 1.6189 | N1 | 1.0807 | 1.7799 | N | 1.404 | 13.02 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 47 | 10 | 42391.55 | 2 | 2 | N-1 | 1.17 | 1.12 | N2 | 1.2083 | 0.92751 | N1 | 1.1652 | 1.1181 | N | 1.6235 | 14.4667 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 48 | 144 | 36864.7 | 2 | 6 | N-1 | 8.29 | 7.23 | N2 | 8.8661 | 1.3566 | N1 | 8.291 | 7.2336 | N | 8.3638 | 14.7056 | 0 | 0.2 | 0 | 0 | 0.2 | 0
| 49 | 5 | 32176.46 | 1 | 3 | N-1 | 0.78 | 0.69 | N2 | 0.84651 | 0.32081 | N1 | 0.78327 | 0.69164 | N | 0.80966 | 2.4809 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 50 | 39 | 37694.51 | 2 | 2 | N-1 | 2.69 | 1.57 | N2 | 2.7914 | 0.7858 | N1 | 2.6949 | 1.5675 | N | 4.5259 | 56.42 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 51 | 8 | 38350 | 1 | 1 | N-1 | 0.87 | 1.33 | N2 | 1.0435 | 1.439 | N1 | 0.87331 | 1.3308 | N | 1.0442 | 9.0404 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 52 | 42 | 38401.47 | 2 | 3 | N-1 | 3.12 | 3.36 | N2 | 3.2859 | 1.4585 | N1 | 3.1165 | 3.3637 | N | 3.6826 | 21.534 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 53 | 22 | 34311.06 | 1 | 1 | N-1 | 1.66 | 0.53 | N2 | 1.9573 | 0.44327 | N1 | 1.6562 | 0.52864 | N | 2.1788 | 24.8611 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 54 | 122 | 35530.24 | 1 | 2 | N-2 | 5.73 | 2.46 | N2 | 5.7309 | 2.4581 | N1 | 5.7812 | 11.1427 | N | 11.1477 | 174.4754 | 0.6 | 0 | 0 | 0.6 | 0 | 0
| 55 | 122 | 35530.24 | 2 | 2 | N-1 | 5.56 | 4.9 | N2 | 5.7309 | 2.4581 | N1 | 5.561 | 4.9034 | N | 11.2647 | 176.4934 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 56 | 39 | 40708.41 | 2 | 3 | N-1 | 2.98 | 3.12 | N2 | 3.1375 | 1.1933 | N1 | 2.9779 | 3.1234 | N | 3.5375 | 19.9958 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 57 | 6 | 29313.64 | 1 | 1 | N-1 | 0.72 | 1 | N2 | 0.85771 | 1.0792 | N1 | 0.71623 | 0.9981 | N | 0.78125 | 6.7803 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 58 | 40 | 35796.16 | 2 | 2 | N-1 | 2.73 | 1.61 | N2 | 2.8344 | 0.80595 | N1 | 2.735 | 1.6077 | N | 4.5098 | 57.8667 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 59 | 246 | 40211.29 | 2 | 2 | N-1 | 8.81 | 9.89 | N2 | 9.0032 | 3.9412 | N1 | 8.8103 | 9.8871 | N | 22.1719 | 355.8801 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 60 | 9 | 33775.2 | 2 | 2 | N-1 | 1.08 | 1.78 | N2 | 1.1186 | 1.6189 | N1 | 1.0781 | 1.7799 | N | 1.3851 | 13.02 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 61 | 51 | 39210.77 | 2 | 3 | N-1 | 3.53 | 0.91 | N2 | 3.7126 | 0.30949 | N1 | 3.5319 | 0.91415 | N | 4.2589 | 26.1484 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 62 | 462 | 39506.97 | 3 | 7 | N-1 | 18.37 | 1 | N2 | 19.1067 | 1.4626 | N1 | 18.3731 | 0.99869 | N | 18.7921 | 29.1371 | 0 | 0.2 | 0 | 0 | 0 | 0
| 63 | 153 | 44829.77 | 0 | 5 | N-1 | 7.32 | 2.72 | N2 | 7.4078 | 0.95287 | N1 | 7.3179 | 2.7236 | N | 7.3366 | 7.208 | 0 | 0 | 0 | 0 | 0.1 | 0
| 64 | 62 | 44829.77 | 2 | 1 | N-1 | 3.24 | 1.28 | N2 | 3.7405 | 0.99331 | N1 | 3.2362 | 1.2765 | N | 5.8145 | 71.0886 | 0 | 0 | 0 | 0 | 0.2 | 0
| 65 | 74 | 38005.74 | 2 | 2 | N-1 | 4.04 | 2.97 | N2 | 4.1751 | 1.1856 | N1 | 4.0434 | 2.9742 | N | 7.6872 | 107.0534 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 66 | 33 | 43962.19 | 0 | 1 | N-1 | 1.91 | 0.67 | N2 | 2.2407 | 0.51924 | N1 | 1.9071 | 0.66894 | N | 3.0583 | 35.343 | 0 | 0 | 0 | 0 | 0.2 | 0
| 67 | 25 | 43962.19 | 2 | 3 | N-1 | 2.24 | 2.67 | N2 | 2.3698 | 1.5009 | N1 | 2.2421 | 2.6659 | N | 2.6138 | 12.8178 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 68 | 66 | 35178.34 | 3 | 3 | N-1 | 4.14 | 2.25 | N2 | 4.2616 | 0.54196 | N1 | 4.1408 | 2.2528 | N | 4.9287 | 30.4387 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 69 | 69 | 33237.78 | 2 | 3 | N-1 | 4.26 | 4 | N2 | 4.4847 | 0.70353 | N1 | 4.2638 | 3.9995 | N | 5.1012 | 35.3772 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 70 | 10 | 33951.07 | 2 | 2 | N-1 | 1.15 | 1.98 | N2 | 1.1977 | 1.7987 | N1 | 1.1543 | 1.9776 | N | 1.5014 | 14.4667 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 71 | 283 | 36345.95 | 2 | 2 | N-1 | 9.61 | 11.37 | N2 | 9.8378 | 4.534 | N1 | 9.6136 | 11.3742 | N | 23.49 | 409.4067 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 72 | 256 | 38808.21 | 3 | 4 | N-1 | 16.22 | 5.39 | N2 | 17.9713 | 1.2704 | N1 | 16.221 | 5.3892 | N | 17.1227 | 38.9547 | 0 | 0.2 | 0 | 0 | 0.1 | 0
| 73 | 10 | 44548.95 | 1 | 2 | N-1 | 1.17 | 1.62 | N2 | 1.2103 | 0.92751 | N1 | 1.1747 | 1.6167 | N | 1.6298 | 14.3013 | 0 | 0.8 | 0 | 0 | 0.2 | 0
| 74 | 30 | 35892.2 | 2 | 2 | N-1 | 2.29 | 1.21 | N2 | 2.3703 | 0.60446 | N1 | 2.285 | 1.2057 | N | 3.5865 | 43.4 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 75 | 692 | 41373.9 | 4 | 3 | N-1 | 8.49 | 2.46 | N2 | 8.5185 | 0.92851 | N1 | 8.4911 | 2.4591 | N | 10.7498 | 65.664 | 0 | 0 | 0 | 0 | 0.1 | 0
| 76 | 917 | 34631.49 | 5 | 7 | N-1 | 10.87 | 1.09 | N2 | 10.8749 | 1.085 | N1 | 10.8745 | 1.0854 | N | 10.9596 | 5.8692 | 0 | 0 | 0 | 0 | 0 | 0
| 77 | 930 | 38808.21 | 6 | 7 | N-1 | 11.27 | 1.18 | N2 | 11.2701 | 1.1822 | N1 | 11.2698 | 1.1828 | N | 11.3713 | 5.7565 | 0 | 0 | 0 | 0 | 0 | 0
| 78 | 1263 | 38534.2 | 5 | 10 | N-1 | 16.09 | 7.6 | N2 | 16.1621 | 1.7049 | N1 | 16.0919 | 7.5967 | N | 16.1502 | 10.0217 | 0 | 0.2 | 0 | 0 | 0 | 0
| 79 | 117 | 36519.99 | 3 | 2 | N-1 | 5.47 | 3.97 | N2 | 5.6188 | 1.8658 | N1 | 5.4711 | 3.9683 | N | 10.8798 | 163.232 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 80 | 24 | 35038.31 | 2 | 3 | N-1 | 2.16 | 2.56 | N2 | 2.2948 | 1.5399 | N1 | 2.1602 | 2.5593 | N | 2.4289 | 12.3051 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 81 | 49 | 35038.31 | 2 | 3 | N-1 | 3.43 | 3.92 | N2 | 3.6189 | 0.49961 | N1 | 3.4307 | 3.9243 | N | 4.0321 | 25.123 | 0 | 0.4 | 0 | 0 | 0.2 | 0
| 82 | 6 | 36309.05 | 2 | 2 | N-1 | 0.83 | 1.19 | N2 | 0.86526 | 1.0792 | N1 | 0.83447 | 1.1866 | N | 1.0483 | 8.68 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 83 | 229 | 6050.12 | 3 | 2 | N-1 | 8.17 | 32.46 | N2 | 8.5141 | 4.7548 | N1 | 8.1667 | 32.4604 | N | 9.517 | 319.4884 | 0 | 0.2 | 0 | 0 | 0.3 | 0
| 84 | 940 | 6050.12 | 6 | 4 | N-1 | 24.32 | 49.97 | N2 | 25.1657 | 20.0616 | N1 | 24.3189 | 49.9721 | N | 24.5882 | 149.5957 | 0 | 0.2 | 0 | 0 | 0.2 | 0
| 85 | 201 | 35530.24 | 2 | 2 | N-1 | 7.68 | 8.08 | N2 | 7.8892 | 4.0499 | N1 | 7.6831 | 8.0785 | N | 17.2281 | 290.7801 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 86 | 38 | 38209.75 | 2 | 2 | N-1 | 2.65 | 1.53 | N2 | 2.747 | 0.76565 | N1 | 2.6521 | 1.5273 | N | 4.4602 | 54.9733 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 87 | 85 | 35530.24 | 2 | 4 | N-1 | 5.26 | 4.28 | N2 | 5.5785 | 2.2746 | N1 | 5.2585 | 4.2806 | N | 5.577 | 18.5493 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 88 | 497 | 35546.44 | 3 | 2 | N-1 | 13.99 | 16.86 | N2 | 14.2283 | 7.9255 | N1 | 13.9899 | 16.8569 | N | 37.174 | 693.3874 | 0 | 0.1 | 0 | 0 | 0.2 | 0
| 89 | 96 | 39800.19 | 3 | 3 | N-1 | 5.27 | 3.28 | N2 | 5.401 | 0.53639 | N1 | 5.2744 | 3.2768 | N | 6.6677 | 44.2745 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 90 | 60 | 39800.19 | 0 | 4 | N-1 | 3.74 | 3.05 | N2 | 3.8323 | 1.1055 | N1 | 3.7376 | 3.0528 | N | 3.9047 | 8.5582 | 0 | 0 | 0 | 0 | 0.2 | 0
| 91 | 27 | 39800.19 | 1 | 3 | N-1 | 2.35 | 3.73 | N2 | 2.4835 | 1.7324 | N1 | 2.3501 | 3.7348 | N | 2.6581 | 13.3967 | 0 | 0.9 | 0 | 0 | 0.2 | 0
| 92 | 111 | 38306.25 | 2 | 4 | N-1 | 6.27 | 4.55 | N2 | 6.6188 | 1.2574 | N1 | 6.2662 | 4.5529 | N | 6.766 | 24.2232 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 93 | 30 | 38306.25 | 2 | 2 | N-1 | 2.29 | 1.21 | N2 | 2.3718 | 0.60446 | N1 | 2.2879 | 1.2057 | N | 3.6913 | 43.4 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 94 | 156 | 39506.97 | 2 | 2 | N-1 | 6.54 | 6.27 | N2 | 6.7162 | 2.4993 | N1 | 6.5429 | 6.2699 | N | 14.7693 | 225.68 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 95 | 174 | 39924.38 | 0 | 2 | N-1 | 6.24 | 5.7 | N2 | 6.3923 | 2.7378 | N1 | 6.2408 | 5.7025 | N | 15.0449 | 238.5674 | 0 | 0 | 0 | 0 | 0.2 | 0
| 96 | 12 | 39924.38 | 1 | 1 | N-1 | 1.14 | 0.96 | N2 | 1.3513 | 1.113 | N1 | 1.1392 | 0.96416 | N | 1.4423 | 13.5606 | 0 | 0.3 | 0 | 0 | 0.2 | 0
| 97 | 186 | 37279.21 | 2 | 4 | N-1 | 8.74 | 2.59 | N2 | 9.1905 | 0.35496 | N1 | 8.7411 | 2.5853 | N | 9.6533 | 40.5903 | 0 | 0.3 | 0 | 0 | 0.1 | 0
| 98 | 38 | 38289.45 | 2 | 4 | N-1 | 3.12 | 1.91 | N2 | 3.3313 | 1.0169 | N1 | 3.1249 | 1.9137 | N | 3.2535 | 8.2926 | 0 | 0.4 | 0 | 0 | 0.1 | 0
| 99 | 13 | 32600.58 | 0 | 2 | N-1 | 1.22 | 1.34 | N2 | 1.2597 | 1.1313 | N1 | 1.2189 | 1.3403 | N | 1.6401 | 17.824 | 0 | 0 | 0 | 0 | 0.2 | 0
| 100 | 13 | 32600.58 | 1 | 2 | N-1 | 1.36 | 2.1 | N2 | 1.4121 | 1.2058 | N1 | 1.3638 | 2.1018 | N | 1.7782 | 18.5916 | 0 | 0.8 | 0 | 0 | 0.2 | 0

## check_res1
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## summary_MWh
N-1 EUE (MWh) | DR | out23_0 | _input0 | basecase | base_bsp96LDC | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130 |  | If current std is N-x, | x
Albury 132 kV | 4.1977 | 4.1984 | 4.1984 | 12.1426 | 12.1426 | 12.1426 | 20.6949 | 0.69908 | 8.455 | 15.8685 | 8.4998 | 15.7854 | 12.1426 | 12.1426 | 10.9096 | 13.3799 | 12.1426 | 12.1426 | 12.1426 | 12.1426 | 0.69908 | 20.6949 | 0.69908 | 20.6949 | x | Albury 132 kV | 1
ANM 132 kV | 24.997 | 25.0066 | 25.0066 | 6.593 | 6.593 | 6.593 | 8.5365 | 6.593 | 5.5159 | 8.6665 | 5.9756 | 8.5709 | 6.593 | 6.593 | 7.4862 | 7.279 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 |  | ANM 132 kV | 1
Armidale 66 kV | 1.592 | 1.592 | 1.592 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.0522 | 1.2176 | 0.88399 | 1.6417 | 1.2629 | 1.2629 | 1.1188 | 1.4109 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 5.3625 |  | Armidale 66 kV | 1
Balranald 22 kV | 2.4698 | 2.4703 | 2.4703 | 2.8048 | 2.8048 | 2.8048 | 11.3505 | 2.8048 | 1.9747 | 3.6349 | 7.9453 | 3.6463 | 2.8048 | 11.3505 | 10.2158 | 3.0852 | 2.8048 | 2.8048 | 2.8048 | 2.8048 | 2.8048 | 11.3505 | 2.8048 | 11.3505 |  | Balranald 22 kV | 0
Beaconsfield 132 kV | 6.5465 | 6.547 | 6.547 | 0.27224 | 0.27224 | 6.9859 | 0.27224 | 0.27224 | 0.22815 | 0.31632 | 3.9466 | 0.35391 | 0.27224 | 5.638 | 5.0694 | 0.2995 | 5.638 | 0.27224 | 0.27224 | 5.638 | 0.27224 | 5.638 | 0.27224 | 5.638 |  | Beaconsfield 132 kV | 2
Beryl 66 kV | 2.6123 | 2.6124 | 2.6124 | 2.088 | 2.088 | 2.088 | 10.6702 | 2.088 | 1.6244 | 2.7068 | 7.4692 | 2.7145 | 2.088 | 10.6702 | 9.5967 | 2.3065 | 10.6702 | 2.088 | 2.088 | 2.088 | 2.088 | 10.6702 | 2.088 | 10.6702 |  | Beryl 66 kV | 1
Boambee South 132 kV | 0.84396 | 0.84402 | 0.84402 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 2.3929 | 4.463 | 2.398 | 4.4534 | 3.4257 | 3.4257 | 3.081 | 3.7708 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 0.74915 | 3.4257 |  | Boambee South 132 kV | 1
Boggabri East | 2.632 | 2.6323 | 2.6323 | 7.5519 | 7.5519 | 7.5519 | 23.2903 | 7.5519 | 5.3498 | 9.7579 | 16.3032 | 9.8175 | 7.5519 | 23.2903 | 20.9555 | 8.3093 | 7.5519 | 7.5519 | 7.5519 | 7.5519 | 7.5519 | 23.2903 | 7.5519 | 23.2903 |  | Boggabri East | -1
Boggabri North | 4.9351 | 4.9356 | 4.9356 | 14.1599 | 14.1599 | 14.1599 | 27.5951 | 14.1599 | 10.0309 | 18.2961 | 9.9119 | 18.4078 | 14.1599 | 14.1599 | 12.7406 | 15.58 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 27.5951 |  | Boggabri North | -1
Brandy Hill 132 kV | 1.118 | 1.1181 | 1.1181 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.58058 | 1.15 | 0.59804 | 1.1106 | 0.85434 | 0.85434 | 0.75639 | 0.95509 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 |  | Brandy Hill 132 kV | -1
Broken Hill 22 kV | 1.5527 | 1.5527 | 1.5527 | 3.9777 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 2.804 | 5.1514 | 8.2922 | 5.171 | 3.9777 | 11.846 | 10.6412 | 4.3817 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 11.846 |  | Broken Hill 22 kV | 0
Broken Hill 220 kV | 49.266 | 0.93246 | 0.93246 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 0.83397 | 1.5488 | 0.83397 | 1.5488 | 1.1914 | 1.1914 | 1.0723 | 1.3105 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 |  | Broken Hill 220 kV | 0
Canberra 132 kV Note 3 | 8.0808 | 8.0811 | 8.0811 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 3.7673 | 6.1581 | 3.4564 | 6.4191 | 4.9378 | 4.9378 | 4.4176 | 5.4638 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 |  | Canberra 132 kV Note 3 | 1
Casino 132 kV | 0.64878 | 0.64878 | 0.64878 | 1.4112 | 1.4112 | 1.4112 | 3.4388 | 1.4112 | 0.98784 | 1.8345 | 2.4071 | 1.8345 | 1.4112 | 1.4112 | 3.095 | 1.5523 | 1.4112 | 1.4112 | 1.4112 | 1.4112 | 1.4112 | 3.4388 | 1.4112 | 3.4388 |  | Casino 132 kV | 0
Coffs Harbour 66 kV | 2.6914 | 2.6914 | 2.6914 | 1.4543 | 1.4543 | 1.4543 | 2.4742 | 0.60435 | 1.8074 | 0.74931 | 1.7319 | 0.78566 | 1.4543 | 1.4543 | 1.2943 | 1.6174 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 |  | Coffs Harbour 66 kV | 1
Coleambally 132 kV | 1.4534 | 1.4536 | 1.4536 | 2.1305 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 1.4893 | 2.7734 | 2.3462 | 2.7697 | 2.1305 | 3.3518 | 3.0155 | 2.3446 | 3.3518 | 2.1305 | 2.1305 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 3.3518 |  | Coleambally 132 kV | 1
Cooma 11 kV | 1.0618 | 1.0627 | 1.0627 | 2.5577 | 2.5577 | 2.5577 | 3.6976 | 0.28407 | 2.6074 | 2.0821 | 2.5883 | 2.0901 | 2.5577 | 2.5577 | 2.2999 | 2.816 | 2.5577 | 2.5577 | 2.5577 | 2.5577 | 1.3079 | 2.5577 | 1.3079 | 2.5577 |  | Cooma 11 kV | -1
Cooma 66 kV | 1.7152 | 1.7166 | 1.7166 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.3259 | 2.4156 | 1.3085 | 2.4301 | 1.8693 | 1.8693 | 1.6809 | 2.058 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 |  | Cooma 66 kV | 1
Cooma 132 kV | 6.1492 | 1.6386 | 1.6386 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 2.614 | 4.8831 | 2.6217 | 4.8689 | 3.7453 | 3.7453 | 3.3676 | 4.1237 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 |  | Cooma 132 kV | 1
Cowra 66 kV | 3.197 | 3.1991 | 3.1991 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 3.1239 | 5.2221 | 2.917 | 5.4174 | 4.1672 | 4.1672 | 3.7445 | 4.5913 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 |  | Cowra 66 kV | 1
Dapto 132 kV | 9.1755 | 9.1777 | 9.1777 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 12.9148 | 24.2081 | 12.9501 | 24.0501 | 18.5001 | 18.5001 | 16.5681 | 20.4504 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 |  | Dapto 132 kV | 1
Darlington Point 132 kV Note 3 | 1.9205 | 1.9221 | 1.9221 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.41537 | 0.75886 | 0.41098 | 0.76325 | 0.58712 | 0.58712 | 0.52842 | 0.64581 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 |  | Darlington Point 132 kV Note 3 | 1
Deniliquin 66 kV | 1.9291 | 1.9292 | 1.9292 | 6.985 | 6.985 | 6.985 | 6.985 | 1.418 | 4.9482 | 9.0306 | 4.8895 | 1.8434 | 1.418 | 6.985 | 6.2822 | 1.5852 | 6.985 | 6.985 | 6.985 | 6.985 | 1.418 | 6.985 | 1.418 | 6.985 |  | Deniliquin 66 kV | 1
Dorrigo 132 kV | 0.85493 | 0.85522 | 0.85522 | 0.83304 | 0.83304 | 0.83304 | 4.2311 | 0.72302 | 0.50612 | 1.083 | 0.50612 | 1.083 | 0.83304 | 0.83304 | 0.74977 | 0.91632 | 0.83304 | 0.83304 | 0.83304 | 0.83304 | 0.72302 | 0.83304 | 0.72302 | 0.83304 |  | Dorrigo 132 kV | 0
Finley 132 kV | 2.4597 | 0.65546 | 0.65546 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.0944 | 3.9066 | 2.099 | 3.8981 | 2.9986 | 2.9986 | 2.6969 | 3.3007 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 0.60964 | 2.9986 |  | Finley 132 kV | 1
Finley 66 kV | 0.80378 | 0.80383 | 0.80383 | 1.5862 | 1.5862 | 1.5862 | 5.1027 | 0.38403 | 2.2082 | 2.052 | 3.5719 | 2.0621 | 1.5862 | 1.5862 | 3.2982 | 1.7463 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 0.38403 | 3.6667 | 0.38403 | 3.6667 |  | Finley 66 kV | 1
Forbes 66 kV | 1.3262 | 1.3263 | 1.3263 | 4.771 | 4.771 | 4.771 | 4.771 | 0.93854 | 3.3799 | 6.1681 | 3.3397 | 6.2023 | 4.771 | 4.771 | 4.2909 | 5.2517 | 4.771 | 4.771 | 4.771 | 4.771 | 0.93854 | 4.771 | 0.93854 | 4.771 |  | Forbes 66 kV | 1
Gadara (132 kV & 11 kV) | 17.479 | 17.4801 | 17.4801 | 6.7941 | 6.7941 | 6.7941 | 11.487 | 6.7941 | 4.8002 | 8.7992 | 4.7559 | 8.8324 | 6.7941 | 6.7941 | 6.1094 | 7.4802 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 90.2109 |  | Gadara (132 kV & 11 kV) | 1
Glen Innes 66 kV | 1.2788 | 1.2796 | 1.2796 | 2.0923 | 2.0923 | 2.0923 | 3.504 | 2.0923 | 1.5084 | 2.6788 | 2.4528 | 2.72 | 2.0923 | 3.504 | 3.1511 | 2.3032 | 3.504 | 2.0923 | 2.0923 | 2.0923 | 1.3116 | 3.504 | 2.0923 | 3.504 |  | Glen Innes 66 kV | 1
Griffith 33 kV | 2.9845 | 2.9847 | 2.9847 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 4.7197 | 8.7227 | 4.7006 | 8.7297 | 6.7152 | 6.7152 | 6.0377 | 7.394 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 1.2732 | 15.1624 |  | Griffith 33 kV | 1
Gunnedah 66 kV | 1.0449 | 1.045 | 1.045 | 3.8736 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 2.7448 | 5.0072 | 2.7115 | 5.0357 | 3.8736 | 3.8736 | 3.4839 | 4.2639 | 3.8736 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 3.8736 | 0.69009 | 3.8736 |  | Gunnedah 66 kV | 1
Hawks Nest 132 kV | 1.3308 | 1.3308 | 1.3308 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 1.5077 | 2.8 | 1.5077 | 2.8 | 2.1538 | 2.1538 | 1.9385 | 2.3691 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 1.8424 |  | Hawks Nest 132 kV | 0
Haymarket 132 kV | 8.041 | 8.0417 | 8.0417 | 0.21612 | 0.21612 | 9.1753 | 0.21612 | 0.21612 | 0.16862 | 0.26361 | 4.7839 | 0.28095 | 0.21612 | 0.21612 | 0.19424 | 0.23776 | 0.21612 | 0.21612 | 0.21612 | 6.8341 | 0.21612 | 6.8341 | 0.21612 | 23.4343 |  | Haymarket 132 kV | 2
Herons Creek | 1.6166 | 1.6167 | 1.6167 | 1.2412 | 1.2412 | 1.2412 | 2.9524 | 0.45 | 2.0667 | 0.585 | 2.0667 | 0.585 | 1.2412 | 2.0573 | 1.8517 | 1.3653 | 2.0573 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 2.0573 | 1.2412 | 2.0573 |  | Herons Creek | 0
Holroyd 132 kV | 17.9376 | 17.9397 | 17.9397 | 57.2802 | 57.2802 | 57.2802 | 57.2802 | 57.2802 | 41.5083 | 73.1686 | 40.0961 | 74.4643 | 57.2802 | 57.2802 | 51.4474 | 63.0377 | 57.2802 | 57.2802 | 2.0848 | 57.2802 | 48.291 | 57.2802 | 2.0848 | 57.2802 |  | Holroyd 132 kV | 1
Ilford 132 kV | 1.4249 | 1.4254 | 1.4254 | 0.82521 | 0.82521 | 0.82521 | 2.1133 | 0.82521 | 1.1553 | 1.0728 | 1.1553 | 1.0728 | 0.82521 | 2.1133 | 1.9021 | 0.9077 | 1.6504 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 2.1133 | 0.82521 | 2.1133 |  | Ilford 132 kV | 0
Ingleburn 66 kV | 1.8801 | 1.8801 | 1.8801 | 4.5481 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 0.59504 | 5.7078 | 3.1837 | 0.78335 | 4.5481 | 4.5481 | 4.0926 | 5.0038 | 4.5481 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 4.5481 | 0.60258 | 4.5481 |  | Ingleburn 66 kV | 1
Inverell 66 kV | 2.8819 | 2.8831 | 2.8831 | 8.6578 | 8.6578 | 8.6578 | 8.6578 | 5.3129 | 4.5418 | 10.81 | 6.0605 | 8.0844 | 5.3129 | 8.6578 | 7.7818 | 6.8503 | 8.6578 | 6.2188 | 8.6578 | 8.6578 | 5.3129 | 8.6578 | 5.3129 | 8.6578 |  | Inverell 66 kV | 1
Kempsey 33 kV | 2.2038 | 2.2038 | 2.2038 | 1.5584 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 1.2358 | 1.8961 | 1.0909 | 2.026 | 1.5584 | 1.5584 | 1.3949 | 1.7237 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 8.0671 |  | Kempsey 33 kV | 1
Koolkhan 66 kV | 2.6198 | 2.6214 | 2.6214 | 6.3276 | 6.3276 | 6.3276 | 7.4603 | 5.3837 | 5.2661 | 6.9772 | 5.2222 | 6.9989 | 6.3276 | 6.3276 | 5.6861 | 6.9711 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 0.3358 | 6.3276 |  | Koolkhan 66 kV | 1
Liddell 330 kV (33 kV supply via Mac Gen) | 2.0474 | 2.0474 | 2.0474 | 0.28796 | 0.28796 | 0.28796 | 1.8246 | 0.28796 | 1.2232 | 0.38478 | 1.2772 | 0.37435 | 0.28796 | 0.49095 | 0.4212 | 0.31969 | 0.49095 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 |  | Liddell 330 kV (33 kV supply via Mac Gen) | 1
Lismore 132 kV Note 3 | 4.264 | 4.2657 | 4.2657 | 2.4687 | 2.4687 | 2.4687 | 17.2288 | 2.4687 | 1.9206 | 3.2003 | 1.9786 | 3.2093 | 2.4687 | 2.8266 | 2.5024 | 2.727 | 2.8266 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 17.2288 |  | Lismore 132 kV Note 3 | 1
Liverpool 132 kV | 2.8851 | 2.8851 | 2.8851 | 7.6165 | 7.6165 | 7.6165 | 20.6133 | 0.86207 | 5.3622 | 7.2639 | 5.3316 | 7.2763 | 5.5972 | 7.6165 | 6.8502 | 6.1626 | 7.6165 | 5.5972 | 7.6165 | 7.6165 | 0.86207 | 7.6165 | 0.86207 | 18.8598 |  | Liverpool 132 kV | 1
Macarthur 132 kV | 1.9759 | 1.9759 | 1.9759 | 3.6496 | 3.6496 | 3.6496 | 7.4825 | 0.7577 | 0.54092 | 7.7675 | 2.5547 | 0.98501 | 3.6496 | 3.6496 | 3.2623 | 4.0417 | 7.4825 | 3.6496 | 3.6496 | 3.6496 | 0.7577 | 7.4825 | 0.7577 | 14.3023 |  | Macarthur 132 kV | 1
Macarthur 66 kV | 0.43366 | 0.43366 | 0.43366 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.42454 | 0.75795 | 0.41387 | 0.76862 | 0.59124 | 0.59124 | 0.53214 | 0.65035 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 5.8942 |  | Macarthur 66 kV | 1
Macksville 132 kV | 1.7796 | 1.7799 | 1.7799 | 1.6928 | 1.6928 | 1.6928 | 2.8782 | 0.79952 | 2.0125 | 2.2046 | 2.0147 | 2.2006 | 1.6928 | 1.6928 | 2.5895 | 1.8631 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 0.79952 | 1.6928 | 0.79952 | 1.6928 |  | Macksville 132 kV | 1
Manildra 132 kV | 1.118 | 1.1181 | 1.1181 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.45925 | 0.93157 | 0.48043 | 0.89223 | 0.68633 | 0.68633 | 0.60865 | 0.76603 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 |  | Manildra 132 kV | 1
Marulan 132 kV | 7.2336 | 7.2336 | 7.2336 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.0081 | 9.5284 | 6.4831 | 12.0401 | 9.2616 | 9.2616 | 8.3288 | 10.1959 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 |  | Marulan 132 kV | 0
Molong 66 kV | 0.6913 | 0.69164 | 0.69164 | 1.2265 | 1.2265 | 1.2265 | 2.1674 | 1.2265 | 0.94053 | 1.5136 | 1.5171 | 1.5944 | 1.2265 | 2.1674 | 1.9493 | 1.3498 | 2.1674 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.1674 | 1.2265 | 2.1674 |  | Molong 66 kV | 0
Moree 66 kV | 1.5674 | 1.5675 | 1.5675 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.5604 | 1.1102 | 0.57729 | 1.0721 | 0.8247 | 0.8247 | 0.73013 | 0.92197 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 |  | Moree 66 kV | 1
Morven 132 kV | 1.3308 | 1.3308 | 1.3308 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.0849 | 1.2392 | 1.4103 | 1.2392 | 1.4103 | 1.7704 | 1.7704 | 1.5934 | 1.9473 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 |  | Morven 132 kV | 0
Mount Piper 66 kV | 3.3622 | 3.3637 | 3.3637 | 5.851 | 5.851 | 5.851 | 5.851 | 0.57173 | 4.4461 | 7.2713 | 4.0957 | 7.6063 | 5.851 | 5.851 | 5.2578 | 6.446 | 5.851 | 5.851 | 5.851 | 5.851 | 0.57173 | 5.851 | 0.57173 | 5.851 |  | Mount Piper 66 kV | 1
Mudgee 132 kV | 0.52864 | 0.52864 | 0.52864 | 2.2316 | 2.2316 | 2.2316 | 2.2316 | 2.2316 | 1.5621 | 2.901 | 1.5621 | 2.901 | 2.2316 | 2.2316 | 2.0085 | 2.4546 | 2.2316 | 2.2316 | 2.2316 | 2.2316 | 0.36159 | 2.2316 | 0.36159 | 4.839 |  | Mudgee 132 kV | 0
Munmorah 132 kV | 11.1424 | 11.1427 | 11.1427 | 14.4819 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 3.0801 | 17.2023 | 10.1373 | 4.5933 | 3.5333 | 14.4819 | 13.0268 | 3.9088 | 14.4819 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 14.4819 | 3.5333 | 26.5934 |  | Munmorah 132 kV | 1
Munmorah 330 kV (via old Power Stn Txs) | 4.903 | 4.9034 | 4.9034 | 9.9648 | 9.9648 | 9.9648 | 9.9648 | 9.9648 | 7.0567 | 12.8904 | 6.9754 | 12.9542 | 9.9648 | 9.9648 | 8.9598 | 10.9718 | 9.9648 | 9.9648 | 9.9648 | 9.9648 | 1.4618 | 9.9648 | 1.4618 | 22.8869 |  | Munmorah 330 kV (via old Power Stn Txs) | -1
Munyang 33 kV | 3.1221 | 3.1234 | 3.1234 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 0.74511 | 1.3662 | 0.73894 | 1.3723 | 1.0556 | 1.0556 | 0.9501 | 1.1612 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 |  | Munyang 33 kV | 0
Murrumbateman 132 kV | 0.9981 | 0.9981 | 0.9981 | 1.6136 | 1.6136 | 1.6136 | 6.8747 | 1.6136 | 1.1295 | 2.0977 | 1.6776 | 2.0977 | 1.6136 | 1.6136 | 1.4523 | 1.7749 | 1.6136 | 1.6136 | 1.6136 | 1.6136 | 1.6136 | 6.8747 | 1.6136 | 6.8747 |  | Murrumbateman 132 kV | 0
Murrumburrah 66 kV | 1.6076 | 1.6077 | 1.6077 | 5.5017 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 3.8977 | 7.1127 | 3.8512 | 7.1522 | 5.5017 | 5.5017 | 4.9482 | 6.056 | 5.5017 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 5.5017 | 1.0847 | 5.5017 |  | Murrumburrah 66 kV | 1
Muswellbrook 132 kV | 9.8864 | 9.8871 | 9.8871 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 3.1683 | 5.2791 | 2.8505 | 5.2938 | 4.0722 | 4.0722 | 3.6496 | 4.4982 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 |  | Muswellbrook 132 kV | 1
Nambucca 66 kV | 1.7796 | 1.7799 | 1.7799 | 2.4993 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 1.7671 | 3.2329 | 1.7495 | 3.2491 | 2.4993 | 2.4993 | 2.2487 | 2.75 | 2.4993 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 2.4993 | 1.6852 | 2.4993 |  | Nambucca 66 kV | 1
Narrabri 66 kV | 0.91398 | 0.91415 | 0.91415 | 1.1622 | 1.1622 | 1.1622 | 6.0966 | 0.95635 | 0.84345 | 1.1749 | 0.81351 | 1.2433 | 1.1622 | 1.1622 | 1.025 | 1.055 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 6.0966 |  | Narrabri 66 kV | 1
Newcastle 132 kV | 0.99829 | 0.99869 | 0.99869 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.3921 | 3.0478 | 1.8983 | 3.5255 | 2.7119 | 2.7119 | 2.4313 | 2.9947 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 |  | Newcastle 132 kV | 1
Orange North 132 kV | 7.208 | 2.7236 | 2.7236 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 5.4891 | 10.0096 | 5.4157 | 10.0578 | 7.7367 | 7.7367 | 6.9316 | 8.5489 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 |  | Orange North 132 kV | 1
Orange 66 kV | 1.2765 | 1.2765 | 1.2765 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 0.82782 | 0.81341 | 0.9622 | 0.74308 | 1.0762 | 0.82782 | 1.0615 | 0.93129 | 0.91436 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 |  | Orange 66 kV | 1
Panorama 66 kV | 2.974 | 2.9742 | 2.9742 | 1.9529 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 1.5192 | 2.5315 | 1.5649 | 2.5387 | 1.9529 | 2.2356 | 1.9793 | 2.1572 | 2.2356 | 1.9529 | 1.9529 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 6.0093 |  | Panorama 66 kV | 1
Parkes 132 kV | 4.0585 | 0.66894 | 0.66894 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 2.1652 | 4.6908 | 2.3455 | 4.3559 | 3.3507 | 3.3507 | 2.9385 | 3.7801 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 |  | Parkes 132 kV | 1
Parkes 66 kV | 2.6642 | 2.6659 | 2.6659 | 8.2898 | 8.2898 | 8.2898 | 8.2898 | 0.87157 | 6.0838 | 10.5107 | 5.8029 | 10.7768 | 8.2898 | 8.2898 | 7.4533 | 9.1281 | 8.2898 | 8.2898 | 8.2898 | 8.2898 | 1.5996 | 8.2898 | 1.5996 | 8.2898 |  | Parkes 66 kV | 1
Port Macquarie 33 kV | 2.2524 | 2.2528 | 2.2528 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 4.516 | 8.2914 | 4.4748 | 8.3102 | 6.3925 | 6.3925 | 5.742 | 7.0455 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 0.60157 | 6.3925 |  | Port Macquarie 33 kV | 1
Queanbeyan 66 kV | 3.9991 | 3.9995 | 3.9995 | 1.2061 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 0.85001 | 1.5622 | 5.0273 | 1.5679 | 1.2061 | 7.1819 | 6.441 | 1.3267 | 7.1819 | 1.2061 | 1.2061 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 7.1819 |  | Queanbeyan 66 kV | 1
Raleigh 132 kV | 1.9773 | 1.9776 | 1.9776 | 1.8918 | 1.8918 | 1.8918 | 2.899 | 1.8918 | 2.0276 | 2.4624 | 2.0293 | 2.4594 | 1.8918 | 1.8918 | 1.702 | 2.0818 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 |  | Raleigh 132 kV | 1
Regentville 132 kV | 11.3734 | 11.3742 | 11.3742 | 19.7476 | 19.7476 | 19.7476 | 31.5849 | 19.7476 | 13.9977 | 25.531 | 22.1094 | 25.6719 | 19.7476 | 19.7476 | 17.7564 | 21.7425 | 19.7476 | 19.7476 | 19.7476 | 19.7476 | 1.4236 | 31.5849 | 1.4236 | 31.5849 |  | Regentville 132 kV | 1
Rookwood Road 132 kV | 5.3888 | 5.3892 | 5.3892 | 0.19399 | 0.19399 | 10.0207 | 0.19399 | 0.19399 | 0.81115 | 0.23608 | 0.6113 | 0.25219 | 0.19399 | 0.19399 | 0.16924 | 0.21968 | 0.19399 | 0.19399 | 0.19399 | 8.5716 | 0.19399 | 8.5716 | 0.19399 | 8.5716 |  | Rookwood Road 132 kV | 2
Snowy Adit 132 kV | 1.6166 | 1.6167 | 1.6167 | 2.6538 | 2.6538 | 2.6538 | 2.6538 | 1.4641 | 1.8576 | 2.7065 | 1.8576 | 2.7065 | 2.6538 | 2.6538 | 2.3885 | 2.919 | 2.6538 | 2.6538 | 2.6538 | 2.6538 | 2.0771 | 2.6538 | 2.0771 | 3.8003 |  | Snowy Adit 132 kV | 0
Stroud 132 kV | 1.2057 | 1.2057 | 1.2057 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 2.9842 | 5.5887 | 2.9968 | 5.5654 | 4.2811 | 4.2811 | 3.8477 | 4.7156 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 |  | Stroud 132 kV | 1
Sydney East 132 kV | 2.459 | 2.4591 | 2.4591 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 2.1726 | 4.2849 | 2.2362 | 4.1529 | 3.1945 | 3.1945 | 2.8407 | 3.556 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 22.2734 |  | Sydney East 132 kV | 1
Sydney North 132 kV | 1.085 | 1.0854 | 1.0854 | 0.85754 | 0.85754 | 3.0856 | 0.85754 | 0.85754 | 0.767 | 0.98806 | 0.60028 | 1.1148 | 0.85754 | 0.85754 | 0.79203 | 0.99037 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 |  | Sydney North 132 kV | 2
Sydney South 132 kV | 1.1822 | 1.1828 | 1.1828 | 0.85021 | 0.85021 | 2.8781 | 0.85021 | 0.85021 | 0.77567 | 0.97366 | 0.59515 | 1.1053 | 0.85021 | 0.85021 | 0.79538 | 0.98624 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 |  | Sydney South 132 kV | 2
Sydney West 132 kV | 7.5954 | 7.5967 | 7.5967 | 7.5573 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 0.81424 | 7.9082 | 5.2901 | 1.4545 | 7.5573 | 7.5573 | 6.7724 | 8.3487 | 7.5573 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 7.5573 | 1.1189 | 7.5573 |  | Sydney West 132 kV | 1
Tamworth 66 kV | 3.968 | 3.9683 | 3.9683 | 2.4246 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 1.8863 | 3.1432 | 1.9432 | 3.152 | 2.4246 | 2.4246 | 2.4577 | 2.6783 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 15.514 |  | Tamworth 66 kV | 1
Taree 33 kV | 2.5576 | 2.5593 | 2.5593 | 5.9183 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 4.4154 | 7.4337 | 4.1428 | 7.6938 | 5.9183 | 5.9183 | 5.3199 | 6.5181 | 5.9183 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 5.9183 | 3.66 | 5.9183 |  | Taree 33 kV | 1
Taree 66 kV | 3.9226 | 3.9243 | 3.9243 | 0.91564 | 0.91564 | 0.91564 | 11.2735 | 0.91564 | 0.66544 | 0.92535 | 0.64095 | 1.1903 | 0.91564 | 0.91564 | 0.80757 | 1.0274 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 11.2735 |  | Taree 66 kV | 1
Tenterfield 22 kV | 1.1864 | 1.1866 | 1.1866 | 2.9473 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.0817 | 2.706 | 2.0631 | 1.6422 | 1.2632 | 2.9473 | 2.6519 | 1.39 | 2.9473 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.9473 | 1.2632 | 2.9473 |  | Tenterfield 22 kV | 1
Tomago 132 Note 3 | 32.4598 | 32.4604 | 32.4604 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 22.8124 | 42.4903 | 22.7489 | 42.2479 | 32.4984 | 32.4984 | 28.996 | 36.0571 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 2.81 | 32.4984 |  | Tomago 132 Note 3 | 1
Tomago 330 kV | 49.93 | 49.9721 | 49.9721 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 110.593 | 201.1949 | 108.6327 | 201.7464 | 155.1895 | 155.1895 | 138.0461 | 172.695 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 |  | Tomago 330 kV | 1
Tuggerah 132 kV | 8.0779 | 8.0785 | 8.0785 | 15.2431 | 15.2431 | 15.2431 | 15.2431 | 2.2795 | 10.7952 | 19.7152 | 10.6702 | 19.8161 | 15.2431 | 15.2431 | 13.707 | 16.782 | 15.2431 | 15.2431 | 15.2431 | 15.2431 | 2.6107 | 15.2431 | 2.6107 | 34.3799 |  | Tuggerah 132 kV | 1
Tumut 66 kV | 1.5272 | 1.5273 | 1.5273 | 3.4583 | 3.4583 | 3.4583 | 7.2129 | 1.3719 | 0.93225 | 4.4782 | 2.4208 | 1.7834 | 1.3719 | 3.4583 | 3.1098 | 1.5337 | 3.4583 | 3.4583 | 3.4583 | 3.4583 | 1.3719 | 3.4583 | 1.3719 | 7.2129 |  | Tumut 66 kV | 1
Vales Pt 132 kV | 4.2778 | 4.2806 | 4.2806 | 0.84904 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 1.6369 | 1.0139 | 12.4223 | 1.1038 | 0.84904 | 17.7462 | 15.9523 | 0.94859 | 17.7462 | 0.84904 | 0.84904 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 17.7462 |  | Vales Pt 132 kV | 1
Vineyard 132 kV | 16.8556 | 16.8569 | 16.8569 | 1.683 | 1.683 | 1.683 | 60.1784 | 1.683 | 2.7664 | 2.441 | 42.1249 | 2.1879 | 1.683 | 60.1784 | 54.1271 | 1.9286 | 60.1784 | 1.683 | 1.683 | 1.683 | 1.683 | 60.1784 | 1.683 | 96.7024 |  | Vineyard 132 kV | 1
Wagga 66 kV | 3.2763 | 3.2768 | 3.2768 | 12.3577 | 12.3577 | 12.3577 | 12.3577 | 0.57925 | 8.8731 | 14.9577 | 8.6504 | 15.1529 | 12.3577 | 12.3577 | 11.1086 | 13.6099 | 12.3577 | 12.3577 | 12.3577 | 12.3577 | 1.7012 | 12.3577 | 1.7012 | 12.3577 |  | Wagga 66 kV | 1
Wagga North 132 kV | 2.27 | 3.0528 | 3.0528 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.1238 | 3.6079 | 1.9317 | 3.5875 | 2.7596 | 2.7596 | 2.4791 | 3.0412 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 |  | Wagga North 132 kV | 1
Wagga North 66 kV | 3.733 | 3.7348 | 3.7348 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 3.1673 | 5.015 | 2.8622 | 5.3155 | 4.0889 | 4.0889 | 3.6778 | 4.5004 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 |  | Wagga North 66 kV | 0
Wallerawang 132 kV Note 3 | 4.551 | 4.5529 | 4.5529 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 8.5331 | 15.2405 | 8.3134 | 15.4392 | 11.8764 | 11.8764 | 10.6783 | 13.0769 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 1.6726 | 11.8764 |  | Wallerawang 132 kV Note 3 | 1
Wallerawang 66 kV | 1.2057 | 1.2057 | 1.2057 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.64612 | 1.0496 | 0.59281 | 1.1009 | 0.84687 | 0.84687 | 0.76112 | 0.93287 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 |  | Wallerawang 66 kV | 1
Waratah West 132 kV | 6.2694 | 6.2699 | 6.2699 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.2276 | 1.7333 | 2.8879 | 1.7859 | 3.3166 | 2.5513 | 2.5513 | 2.2586 | 2.4607 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 28.7586 |  | Waratah West 132 kV | 1
Wellington 132 kV Note 3 | 3.2553 | 5.7025 | 5.7025 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 4.1296 | 7.572 | 4.0889 | 7.5936 | 5.8412 | 5.8412 | 5.2351 | 6.4523 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 27.0563 |  | Wellington 132 kV Note 3 | 1
Wellington Town | 0.96416 | 0.96416 | 0.96416 | 4.9655 | 1.486 | 4.9655 | 4.9655 | 1.5589 | 3.4759 | 6.4552 | 3.4759 | 6.4552 | 4.9655 | 4.9655 | 4.4691 | 5.4619 | 4.9655 | 4.9655 | 4.9655 | 4.9655 | 1.5589 | 4.9655 | 0.91791 | 4.9655 |  | Wellington Town | 0
Williamsdale 132 kV Note 3 | 2.5851 | 2.5853 | 2.5853 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 5.4861 | 6.901 | 4.3275 | 8.0368 | 6.1822 | 6.1822 | 5.5509 | 6.8163 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 |  | Williamsdale 132 kV Note 3 | 1
Yanco 33 kV | 1.9124 | 1.9137 | 1.9137 | 8.8597 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 1.5647 | 10.7944 | 6.2018 | 1.5725 | 1.2096 | 8.8597 | 7.9606 | 1.3405 | 8.8597 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 8.8597 | 1.2096 | 8.8597 |  | Yanco 33 kV | 1
Yass 132 kV | 1.5988 | 1.3403 | 1.3403 | 1.2984 | 1.2984 | 1.2984 | 2.5608 | 0.24648 | 1.7845 | 0.33457 | 1.7925 | 0.32042 | 1.2984 | 1.2984 | 1.1653 | 1.4323 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 |  | Yass 132 kV | -1
Yass 66 kV | 2.1015 | 2.1018 | 2.1018 | 1.072 | 1.072 | 1.072 | 3.5196 | 1.072 | 0.847 | 1.3073 | 0.75043 | 1.3937 | 1.072 | 1.072 | 0.95963 | 1.1856 | 1.072 | 1.072 | 1.072 | 1.072 | 1.072 | 3.5196 | 1.072 | 1.072 |  | Yass 66 kV | 0
|  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## summary_mins
N-1 EUE (mins @ avg demand) | DR | out23_0 | _input0 | basecase | base_bsp96LDC | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130 |  | If current std is N-x, | x
Albury 132 kV | 4.015 | 4.0157 | 4.0157 | 13.335 | 13.335 | 13.335 | 22.7271 | 0.76773 | 9.2853 | 17.4268 | 9.3345 | 17.3355 | 13.335 | 13.335 | 11.9809 | 14.6938 | 13.335 | 13.335 | 13.335 | 13.335 | 0.76773 | 22.7271 | 0.76773 | 22.7271 | x | Albury 132 kV | 1
ANM 132 kV | 26.7347 | 26.745 | 26.745 | 5.4189 | 5.4189 | 5.4189 | 7.0163 | 5.4189 | 4.5336 | 7.1232 | 4.9114 | 7.0445 | 5.4189 | 5.4189 | 6.1531 | 5.9827 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 |  | ANM 132 kV | 1
Armidale 66 kV | 4.9289 | 4.9289 | 4.9289 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 4.2928 | 4.9677 | 3.6067 | 6.6981 | 5.1524 | 5.1524 | 4.5646 | 5.7563 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 5.1524 | 21.8789 |  | Armidale 66 kV | 1
Balranald 22 kV | 72.6404 | 72.6556 | 72.6556 | 103.8826 | 103.8826 | 103.8826 | 420.387 | 103.8826 | 73.1381 | 134.627 | 294.2707 | 135.0474 | 103.8826 | 420.387 | 378.3626 | 114.2674 | 103.8826 | 103.8826 | 103.8826 | 103.8826 | 103.8826 | 420.387 | 103.8826 | 420.387 |  | Balranald 22 kV | 0
Beaconsfield 132 kV | 2.4765 | 2.4767 | 2.4767 | 0.082132 | 0.082132 | 2.1076 | 0.082132 | 0.082132 | 0.06883 | 0.09543 | 1.1907 | 0.10677 | 0.082132 | 1.7009 | 1.5294 | 0.090356 | 1.7009 | 0.082132 | 0.082132 | 1.7009 | 0.082132 | 1.7009 | 0.082132 | 1.7009 |  | Beaconsfield 132 kV | 2
Beryl 66 kV | 4.7281 | 4.7284 | 4.7284 | 3.3897 | 3.3897 | 3.3897 | 17.3218 | 3.3897 | 2.637 | 4.3941 | 12.1253 | 4.4066 | 3.3897 | 17.3218 | 15.5791 | 3.7443 | 17.3218 | 3.3897 | 3.3897 | 3.3897 | 3.3897 | 17.3218 | 3.3897 | 17.3218 |  | Beryl 66 kV | 1
Boambee South 132 kV | 4.7281 | 4.7284 | 4.7284 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 11.9762 | 22.3372 | 12.002 | 22.2894 | 17.1457 | 17.1457 | 15.4207 | 18.8731 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 3.7495 | 17.1457 |  | Boambee South 132 kV | 1
Boggabri East | 38.7065 | 38.7103 | 38.7103 | 101.1419 | 101.1419 | 101.1419 | 311.923 | 101.1419 | 71.6491 | 130.6863 | 218.346 | 131.4845 | 101.1419 | 311.923 | 280.6535 | 111.2857 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 311.923 | 101.1419 | 311.923 |  | Boggabri East | -1
Boggabri North | 38.7065 | 38.7104 | 38.7104 | 101.1419 | 101.1419 | 101.1419 | 197.1079 | 101.1419 | 71.6491 | 130.6863 | 70.7994 | 131.4846 | 101.1419 | 101.1419 | 91.0043 | 111.2856 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 101.1419 | 197.1079 |  | Boggabri North | -1
Brandy Hill 132 kV | 13.1528 | 13.1547 | 13.1547 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 3.5912 | 7.1134 | 3.6992 | 6.87 | 5.2846 | 5.2846 | 4.6787 | 5.9078 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 5.2846 | 5.2846 |  | Brandy Hill 132 kV | -1
Broken Hill 22 kV | 4.8071 | 4.8071 | 4.8071 | 13.0845 | 13.0845 | 13.0845 | 38.967 | 13.0845 | 9.2236 | 16.9455 | 27.2769 | 17.0099 | 13.0845 | 38.967 | 35.0038 | 14.4134 | 13.0845 | 13.0845 | 13.0845 | 13.0845 | 13.0845 | 38.967 | 13.0845 | 38.967 |  | Broken Hill 22 kV | 0
Broken Hill 220 kV | 252 | 4.7696 | 4.7696 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 3.0326 | 5.632 | 3.0326 | 5.632 | 4.3323 | 4.3323 | 3.8992 | 4.7654 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 |  | Broken Hill 220 kV | 0
Canberra 132 kV Note 3 | 1.9889 | 1.989 | 1.989 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 0.94476 | 1.5444 | 0.86682 | 1.6098 | 1.2383 | 1.2383 | 1.1079 | 1.3702 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 1.2383 | 1.2383 |  | Canberra 132 kV Note 3 | 1
Casino 132 kV | 2.8269 | 2.8269 | 2.8269 | 6.272 | 6.272 | 6.272 | 15.2833 | 6.272 | 4.3904 | 8.1536 | 10.6984 | 8.1536 | 6.272 | 6.272 | 13.7556 | 6.899 | 6.272 | 6.272 | 6.272 | 6.272 | 6.272 | 15.2833 | 6.272 | 15.2833 |  | Casino 132 kV | 0
Coffs Harbour 66 kV | 5.8636 | 5.8636 | 5.8636 | 3.3875 | 3.3875 | 3.3875 | 5.7632 | 1.4078 | 4.2101 | 1.7454 | 4.0343 | 1.8301 | 3.3875 | 3.3875 | 3.015 | 3.7676 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 3.3875 |  | Coffs Harbour 66 kV | 1
Coleambally 132 kV | 13.1528 | 13.1548 | 13.1548 | 31.4392 | 31.4392 | 31.4392 | 49.4602 | 31.4392 | 21.9776 | 40.9265 | 34.622 | 40.871 | 31.4392 | 49.4602 | 44.4977 | 34.5977 | 49.4602 | 31.4392 | 31.4392 | 31.4392 | 31.4392 | 49.4602 | 31.4392 | 49.4602 |  | Coleambally 132 kV | 1
Cooma 11 kV | 9.609 | 9.617 | 9.617 | 21.8606 | 21.8606 | 21.8606 | 31.6037 | 2.4279 | 22.2853 | 17.7962 | 22.1226 | 17.8638 | 21.8606 | 21.8606 | 19.6571 | 24.0682 | 21.8606 | 21.8606 | 21.8606 | 21.8606 | 11.1786 | 21.8606 | 11.1786 | 21.8606 |  | Cooma 11 kV | -1
Cooma 66 kV | 9.609 | 9.617 | 9.617 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 19.1604 | 34.9069 | 18.909 | 35.1168 | 27.0129 | 27.0129 | 24.2908 | 29.7397 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 |  | Cooma 66 kV | 1
Cooma 132 kV | 14.4688 | 3.8556 | 3.8556 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 7.5404 | 14.0859 | 7.5626 | 14.0448 | 10.8037 | 10.8037 | 9.7142 | 11.8953 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 |  | Cooma 132 kV | 1
Cowra 66 kV | 12.5373 | 12.5454 | 12.5454 | 19.254 | 19.254 | 19.254 | 19.254 | 19.254 | 14.4334 | 24.1282 | 13.4778 | 25.0302 | 19.254 | 19.254 | 17.3009 | 21.2134 | 19.254 | 19.254 | 19.254 | 19.254 | 19.254 | 19.254 | 19.254 | 19.254 |  | Cowra 66 kV | 1
Dapto 132 kV | 1.5945 | 1.5949 | 1.5949 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.0878 | 3.9135 | 2.0935 | 3.8879 | 2.9907 | 2.9907 | 2.6784 | 3.306 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.9907 | 2.9907 |  | Dapto 132 kV | 1
Darlington Point 132 kV Note 3 | 12.5525 | 12.563 | 12.563 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 1.5734 | 2.8745 | 1.5567 | 2.8911 | 2.2239 | 2.2239 | 2.0016 | 2.4462 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 2.2239 | 2.2239 |  | Darlington Point 132 kV Note 3 | 1
Deniliquin 66 kV | 4.7281 | 4.7284 | 4.7284 | 17.5334 | 17.5334 | 17.5334 | 17.5334 | 3.5593 | 12.4208 | 22.6681 | 12.2734 | 4.6271 | 3.5593 | 17.5334 | 15.7693 | 3.9791 | 17.5334 | 17.5334 | 17.5334 | 17.5334 | 3.5593 | 17.5334 | 3.5593 | 17.5334 |  | Deniliquin 66 kV | 1
Dorrigo 132 kV | 33.5268 | 33.538 | 33.538 | 40.3084 | 40.3084 | 40.3084 | 204.7316 | 34.9848 | 24.4897 | 52.4013 | 24.4897 | 52.4013 | 40.3084 | 40.3084 | 36.2792 | 44.3381 | 40.3084 | 40.3084 | 40.3084 | 40.3084 | 34.9848 | 40.3084 | 34.9848 | 40.3084 |  | Dorrigo 132 kV | 0
Finley 132 kV | 14.4688 | 3.8556 | 3.8556 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 11.8553 | 22.1131 | 11.8811 | 22.0649 | 16.973 | 16.973 | 15.2652 | 18.6833 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 3.4508 | 16.973 |  | Finley 132 kV | 1
Finley 66 kV | 4.7281 | 4.7284 | 4.7284 | 10.9737 | 10.9737 | 10.9737 | 35.3004 | 2.6567 | 15.2764 | 14.1957 | 24.7103 | 14.2659 | 10.9737 | 10.9737 | 22.8173 | 12.0809 | 10.9737 | 10.9737 | 10.9737 | 10.9737 | 2.6567 | 25.3665 | 2.6567 | 25.3665 |  | Finley 66 kV | 1
Forbes 66 kV | 4.7281 | 4.7284 | 4.7284 | 17.2113 | 17.2113 | 17.2113 | 17.2113 | 3.3858 | 12.193 | 22.2514 | 12.0479 | 22.3746 | 17.2113 | 17.2113 | 15.4795 | 18.9455 | 17.2113 | 17.2113 | 17.2113 | 17.2113 | 3.3858 | 17.2113 | 3.3858 | 17.2113 |  | Forbes 66 kV | 1
Gadara (132 kV & 11 kV) | 29.3764 | 29.3783 | 29.3783 | 11.1379 | 11.1379 | 11.1379 | 18.8311 | 11.1379 | 7.8691 | 14.4249 | 7.7966 | 14.4793 | 11.1379 | 11.1379 | 10.0153 | 12.2626 | 11.1379 | 11.1379 | 11.1379 | 11.1379 | 11.1379 | 11.1379 | 11.1379 | 147.8867 |  | Gadara (132 kV & 11 kV) | 1
Glen Innes 66 kV | 12.5373 | 12.5454 | 12.5454 | 29.0599 | 29.0599 | 29.0599 | 48.6671 | 29.0599 | 20.9506 | 37.206 | 34.0669 | 37.7778 | 29.0599 | 48.6671 | 43.7654 | 31.9885 | 48.6671 | 29.0599 | 29.0599 | 29.0599 | 18.2168 | 48.6671 | 29.0599 | 48.6671 |  | Glen Innes 66 kV | 1
Griffith 33 kV | 3.99 | 3.9903 | 3.9903 | 10.7157 | 10.7157 | 10.7157 | 10.7157 | 10.7157 | 7.5315 | 13.9192 | 7.501 | 13.9304 | 10.7157 | 10.7157 | 9.6347 | 11.7989 | 10.7157 | 10.7157 | 10.7157 | 10.7157 | 10.7157 | 10.7157 | 2.0318 | 24.1954 |  | Griffith 33 kV | 1
Gunnedah 66 kV | 4.7281 | 4.7284 | 4.7284 | 17.8071 | 17.8071 | 17.8071 | 17.8071 | 3.1723 | 12.618 | 23.0182 | 12.4649 | 23.1492 | 17.8071 | 17.8071 | 16.0157 | 19.601 | 17.8071 | 17.8071 | 17.8071 | 17.8071 | 3.1723 | 17.8071 | 3.1723 | 17.8071 |  | Gunnedah 66 kV | 1
Hawks Nest 132 kV | 19.5705 | 19.5706 | 19.5706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 29.1058 | 54.0535 | 29.1058 | 54.0535 | 41.5795 | 41.5795 | 37.423 | 45.7361 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 35.5674 |  | Hawks Nest 132 kV | 0
Haymarket 132 kV | 2.4765 | 2.4767 | 2.4767 | 0.060572 | 0.060572 | 2.5715 | 0.060572 | 0.060572 | 0.047259 | 0.073882 | 1.3408 | 0.078742 | 0.060572 | 0.060572 | 0.054439 | 0.066637 | 0.060572 | 0.060572 | 0.060572 | 1.9154 | 0.060572 | 1.9154 | 0.060572 | 6.5679 |  | Haymarket 132 kV | 2
Herons Creek | 19.0185 | 19.0205 | 19.0205 | 16.5316 | 16.5316 | 16.5316 | 39.3218 | 5.9933 | 27.5251 | 7.7913 | 27.5251 | 7.7913 | 16.5316 | 27.4004 | 24.6613 | 18.1842 | 27.4004 | 16.5316 | 16.5316 | 16.5316 | 16.5316 | 27.4004 | 16.5316 | 27.4004 |  | Herons Creek | 0
Holroyd 132 kV | 5.2495 | 5.2501 | 5.2501 | 23.8624 | 23.8624 | 23.8624 | 23.8624 | 23.8624 | 17.292 | 30.4814 | 16.7037 | 31.0212 | 23.8624 | 23.8624 | 21.4326 | 26.261 | 23.8624 | 23.8624 | 0.86851 | 23.8624 | 20.1176 | 23.8624 | 0.86851 | 23.8624 |  | Holroyd 132 kV | 1
Ilford 132 kV | 33.5268 | 33.5381 | 33.5381 | 13.1682 | 13.1682 | 13.1682 | 33.7234 | 13.1682 | 18.4356 | 17.1188 | 18.4356 | 17.1188 | 13.1682 | 33.7234 | 30.3522 | 14.4846 | 26.3365 | 13.1682 | 13.1682 | 13.1682 | 13.1682 | 33.7234 | 13.1682 | 33.7234 |  | Ilford 132 kV | 0
Ingleburn 66 kV | 1.6385 | 1.6385 | 1.6385 | 4.0917 | 4.0917 | 4.0917 | 4.0917 | 0.54211 | 0.53532 | 5.135 | 2.8642 | 0.70474 | 4.0917 | 4.0917 | 3.6819 | 4.5016 | 4.0917 | 4.0917 | 4.0917 | 4.0917 | 0.54211 | 4.0917 | 0.54211 | 4.0917 |  | Ingleburn 66 kV | 1
Inverell 66 kV | 9.418 | 9.422 | 9.422 | 30.2897 | 30.2897 | 30.2897 | 30.2897 | 18.5875 | 15.8897 | 37.8193 | 21.2028 | 28.2837 | 18.5875 | 30.2897 | 27.2249 | 23.9661 | 30.2897 | 21.7567 | 30.2897 | 30.2897 | 18.5875 | 30.2897 | 18.5875 | 30.2897 |  | Inverell 66 kV | 1
Kempsey 33 kV | 9.6027 | 9.6027 | 9.6027 | 7.0158 | 7.0158 | 7.0158 | 36.3164 | 7.0158 | 5.5635 | 8.5359 | 4.911 | 9.1205 | 7.0158 | 7.0158 | 6.2796 | 7.7597 | 7.0158 | 7.0158 | 7.0158 | 7.0158 | 7.0158 | 36.3164 | 7.0158 | 36.3164 |  | Kempsey 33 kV | 1
Koolkhan 66 kV | 6.5577 | 6.5618 | 6.5618 | 15.9856 | 15.9856 | 15.9856 | 18.8471 | 13.601 | 13.3039 | 17.6267 | 13.193 | 17.6813 | 15.9856 | 15.9856 | 14.3649 | 17.6113 | 15.9856 | 15.9856 | 15.9856 | 15.9856 | 15.9856 | 15.9856 | 0.84834 | 15.9856 |  | Koolkhan 66 kV | 1
Liddell 330 kV (33 kV supply via Mac Gen) | 6.3387 | 6.3387 | 6.3387 | 1.0718 | 1.0718 | 1.0718 | 6.7915 | 1.0718 | 4.5528 | 1.4322 | 4.754 | 1.3934 | 1.0718 | 1.8274 | 1.5677 | 1.1899 | 1.8274 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718 |  | Liddell 330 kV (33 kV supply via Mac Gen) | 1
Lismore 132 kV Note 3 | 4.8235 | 4.8255 | 4.8255 | 2.6718 | 2.6718 | 2.6718 | 18.6458 | 2.6718 | 2.0786 | 3.4635 | 2.1413 | 3.4733 | 2.6718 | 3.059 | 2.7082 | 2.9513 | 3.059 | 2.6718 | 2.6718 | 2.6718 | 2.6718 | 2.6718 | 2.6718 | 18.6458 |  | Lismore 132 kV Note 3 | 1
Liverpool 132 kV | 0.90031 | 0.90033 | 0.90033 | 2.9187 | 2.9187 | 2.9187 | 7.899 | 0.33035 | 2.0548 | 2.7835 | 2.0431 | 2.7883 | 2.1448 | 2.9187 | 2.625 | 2.3615 | 2.9187 | 2.1448 | 2.9187 | 2.9187 | 0.33035 | 2.9187 | 0.33035 | 7.2271 |  | Liverpool 132 kV | 1
Macarthur 132 kV | 0.78007 | 0.78007 | 0.78007 | 2.8759 | 2.8759 | 2.8759 | 5.8964 | 0.59708 | 0.42626 | 6.121 | 2.0132 | 0.77621 | 2.8759 | 2.8759 | 2.5708 | 3.185 | 5.8964 | 2.8759 | 2.8759 | 2.8759 | 0.59708 | 5.8964 | 0.59708 | 11.2705 |  | Macarthur 132 kV | 1
Macarthur 66 kV | 0.28662 | 0.28662 | 0.28662 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 0.33455 | 0.59728 | 0.32614 | 0.60569 | 0.46591 | 0.46591 | 0.41934 | 0.51249 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 0.46591 | 4.6448 |  | Macarthur 66 kV | 1
Macksville 132 kV | 23.2625 | 23.2663 | 23.2663 | 22.5551 | 22.5551 | 22.5551 | 38.3498 | 10.6532 | 26.8152 | 29.375 | 26.8448 | 29.3217 | 22.5551 | 22.5551 | 34.5034 | 24.8249 | 22.5551 | 22.5551 | 22.5551 | 22.5551 | 10.6532 | 22.5551 | 10.6532 | 22.5551 |  | Macksville 132 kV | 1
Manildra 132 kV | 13.1528 | 13.1547 | 13.1547 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 3.4196 | 6.9365 | 3.5773 | 6.6436 | 5.1104 | 5.1104 | 4.532 | 5.7039 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 |  | Manildra 132 kV | 1
Marulan 132 kV | 5.9098 | 5.9098 | 5.9098 | 8.751 | 8.751 | 8.751 | 8.751 | 8.751 | 8.5114 | 9.0031 | 6.1257 | 11.3763 | 8.751 | 8.751 | 7.8697 | 9.6337 | 8.751 | 8.751 | 8.751 | 8.751 | 8.751 | 8.751 | 8.751 | 8.751 |  | Marulan 132 kV | 0
Molong 66 kV | 16.2658 | 16.2739 | 16.2739 | 35.1928 | 35.1928 | 35.1928 | 62.1911 | 35.1928 | 26.9879 | 43.433 | 43.5337 | 45.7509 | 35.1928 | 62.1911 | 55.9352 | 38.7329 | 62.1911 | 35.1928 | 35.1928 | 35.1928 | 35.1928 | 62.1911 | 35.1928 | 62.1911 |  | Molong 66 kV | 0
Moree 66 kV | 4.7281 | 4.7284 | 4.7284 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 2.3497 | 4.6548 | 2.4205 | 4.4953 | 3.4579 | 3.4579 | 3.0613 | 3.8657 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 3.4579 | 3.4579 |  | Moree 66 kV | 1
Morven 132 kV | 19.5705 | 19.5706 | 19.5706 | 32.355 | 32.355 | 32.355 | 32.355 | 19.8272 | 22.6485 | 25.7753 | 22.6485 | 25.7753 | 32.355 | 32.355 | 29.1207 | 35.5895 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 |  | Morven 132 kV | 0
Mount Piper 66 kV | 9.418 | 9.422 | 9.422 | 17.0832 | 17.0832 | 17.0832 | 17.0832 | 1.6693 | 12.9814 | 21.23 | 11.9583 | 22.2082 | 17.0832 | 17.0832 | 15.3514 | 18.8205 | 17.0832 | 17.0832 | 17.0832 | 17.0832 | 1.6693 | 17.0832 | 1.6693 | 17.0832 |  | Mount Piper 66 kV | 1
Mudgee 132 kV | 2.8269 | 2.827 | 2.827 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 9.433 | 17.5184 | 9.433 | 17.5184 | 13.4757 | 13.4757 | 12.1286 | 14.8228 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 2.1835 | 13.4757 | 2.1835 | 29.2212 |  | Mudgee 132 kV | 0
Munmorah 132 kV | 10.7448 | 10.7452 | 10.7452 | 18.7217 | 18.7217 | 18.7217 | 18.7217 | 4.5677 | 3.9819 | 22.2386 | 13.1052 | 5.938 | 4.5677 | 18.7217 | 16.8407 | 5.0532 | 18.7217 | 18.7217 | 18.7217 | 18.7217 | 4.5677 | 18.7217 | 4.5677 | 34.3791 |  | Munmorah 132 kV | 1
Munmorah 330 kV (via old Power Stn Txs) | 4.7281 | 4.7284 | 4.7284 | 11.138 | 11.138 | 11.138 | 11.138 | 11.138 | 7.8875 | 14.4081 | 7.7966 | 14.4794 | 11.138 | 11.138 | 10.0146 | 12.2636 | 11.138 | 11.138 | 11.138 | 11.138 | 1.6339 | 11.138 | 1.6339 | 25.5814 |  | Munmorah 330 kV (via old Power Stn Txs) | -1
Munyang 33 kV | 9.418 | 9.422 | 9.422 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 130.7211 | 239.6772 | 129.6386 | 240.7579 | 185.1982 | 185.1982 | 166.6842 | 203.714 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 185.1982 | 185.1982 |  | Munyang 33 kV | 0
Murrumbateman 132 kV | 19.5705 | 19.5706 | 19.5706 | 48.8967 | 48.8967 | 48.8967 | 208.3255 | 48.8967 | 34.2276 | 63.5658 | 50.8361 | 63.5658 | 48.8967 | 48.8967 | 44.0088 | 53.7845 | 48.8967 | 48.8967 | 48.8967 | 48.8967 | 48.8967 | 208.3255 | 48.8967 | 208.3255 |  | Murrumbateman 132 kV | 0
Murrumburrah 66 kV | 4.7281 | 4.7284 | 4.7284 | 17.4953 | 17.4953 | 17.4953 | 17.4953 | 3.4495 | 12.3945 | 22.6182 | 12.2467 | 22.7439 | 17.4953 | 17.4953 | 15.7351 | 19.2581 | 17.4953 | 17.4953 | 17.4953 | 17.4953 | 3.4495 | 17.4953 | 3.4495 | 17.4953 |  | Murrumburrah 66 kV | 1
Muswellbrook 132 kV | 4.7281 | 4.7284 | 4.7284 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 1.6399 | 2.7324 | 1.4754 | 2.74 | 2.1077 | 2.1077 | 1.889 | 2.3282 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 2.1077 | 2.1077 |  | Muswellbrook 132 kV | 1
Nambucca 66 kV | 23.2625 | 23.2663 | 23.2663 | 53.6907 | 53.6907 | 53.6907 | 53.6907 | 36.2015 | 37.9613 | 69.4505 | 37.5835 | 69.7979 | 53.6907 | 53.6907 | 48.3076 | 59.0771 | 53.6907 | 53.6907 | 53.6907 | 53.6907 | 36.2015 | 53.6907 | 36.2015 | 53.6907 |  | Nambucca 66 kV | 1
Narrabri 66 kV | 2.1084 | 2.1088 | 2.1088 | 2.8299 | 2.8299 | 2.8299 | 14.8456 | 2.3288 | 2.0539 | 2.8609 | 1.9809 | 3.0274 | 2.8299 | 2.8299 | 2.4958 | 2.569 | 2.8299 | 2.8299 | 2.8299 | 2.8299 | 2.8299 | 2.8299 | 2.8299 | 14.8456 |  | Narrabri 66 kV | 1
Newcastle 132 kV | 0.25421 | 0.25431 | 0.25431 | 1.161 | 1.161 | 1.161 | 1.161 | 1.161 | 1.0241 | 1.3048 | 0.8127 | 1.5093 | 1.161 | 1.161 | 1.0408 | 1.2821 | 1.161 | 1.161 | 1.161 | 1.161 | 1.161 | 1.161 | 1.161 | 1.161 |  | Newcastle 132 kV | 1
Orange North 132 kV | 5.5425 | 2.0942 | 2.0942 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 3.0993 | 5.6517 | 3.0579 | 5.6789 | 4.3684 | 4.3684 | 3.9138 | 4.827 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 4.3684 | 4.3684 |  | Orange North 132 kV | 1
Orange 66 kV | 2.4222 | 2.4222 | 2.4222 | 2.4269 | 2.4269 | 2.4269 | 2.4269 | 1.8926 | 1.8596 | 2.1998 | 1.6989 | 2.4604 | 1.8926 | 2.4269 | 2.1291 | 2.0904 | 2.4269 | 2.4269 | 2.4269 | 2.4269 | 2.4269 | 2.4269 | 2.4269 | 2.4269 |  | Orange 66 kV | 1
Panorama 66 kV | 4.7281 | 4.7284 | 4.7284 | 3.5688 | 3.5688 | 3.5688 | 10.9819 | 3.5688 | 2.7763 | 4.6263 | 2.8599 | 4.6395 | 3.5688 | 4.0856 | 3.6171 | 3.9422 | 4.0856 | 3.5688 | 3.5688 | 3.5688 | 3.5688 | 10.9819 | 3.5688 | 10.9819 |  | Panorama 66 kV | 1
Parkes 132 kV | 14.4688 | 2.3848 | 2.3848 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 5.3602 | 11.6129 | 5.8067 | 10.7838 | 8.2952 | 8.2952 | 7.2747 | 9.3582 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 |  | Parkes 132 kV | 1
Parkes 66 kV | 12.5373 | 12.5454 | 12.5454 | 42.5702 | 42.5702 | 42.5702 | 42.5702 | 4.4757 | 31.2417 | 53.9746 | 29.7991 | 55.3412 | 42.5702 | 42.5702 | 38.2742 | 46.8751 | 42.5702 | 42.5702 | 42.5702 | 42.5702 | 8.2141 | 42.5702 | 8.2141 | 42.5702 |  | Parkes 66 kV | 1
Port Macquarie 33 kV | 4.015 | 4.0157 | 4.0157 | 13.1818 | 13.1818 | 13.1818 | 13.1818 | 13.1818 | 9.3124 | 17.0974 | 9.2272 | 17.1363 | 13.1818 | 13.1818 | 11.8405 | 14.5283 | 13.1818 | 13.1818 | 13.1818 | 13.1818 | 13.1818 | 13.1818 | 1.2405 | 13.1818 |  | Port Macquarie 33 kV | 1
Queanbeyan 66 kV | 6.8186 | 6.8192 | 6.8192 | 2.202 | 2.202 | 2.202 | 13.1121 | 2.202 | 1.5519 | 2.8522 | 9.1784 | 2.8626 | 2.202 | 13.1121 | 11.7594 | 2.4221 | 13.1121 | 2.202 | 2.202 | 2.202 | 2.202 | 13.1121 | 2.202 | 13.1121 |  | Queanbeyan 66 kV | 1
Raleigh 132 kV | 23.2625 | 23.2662 | 23.2662 | 31.1838 | 31.1838 | 31.1838 | 47.7857 | 31.1838 | 33.4218 | 40.5893 | 33.45 | 40.5391 | 31.1838 | 31.1838 | 28.0549 | 34.3154 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 |  | Raleigh 132 kV | 1
Regentville 132 kV | 4.7281 | 4.7284 | 4.7284 | 12.1162 | 12.1162 | 12.1162 | 19.379 | 12.1162 | 8.5883 | 15.6646 | 13.5653 | 15.7511 | 12.1162 | 12.1162 | 10.8945 | 13.3402 | 12.1162 | 12.1162 | 12.1162 | 12.1162 | 0.87347 | 19.379 | 0.87347 | 19.379 |  | Regentville 132 kV | 1
Rookwood Road 132 kV | 2.4765 | 2.4767 | 2.4767 | 0.086603 | 0.086603 | 4.4735 | 0.086603 | 0.086603 | 0.36212 | 0.10539 | 0.2729 | 0.11258 | 0.086603 | 0.086603 | 0.075554 | 0.098071 | 0.086603 | 0.086603 | 0.086603 | 3.8266 | 0.086603 | 3.8266 | 0.086603 | 3.8266 |  | Rookwood Road 132 kV | 2
Snowy Adit 132 kV | 19.0185 | 19.0205 | 19.0205 | 51.3629 | 51.3629 | 51.3629 | 51.3629 | 28.338 | 35.9539 | 52.3841 | 35.9539 | 52.3841 | 51.3629 | 51.3629 | 46.2283 | 56.4974 | 51.3629 | 51.3629 | 51.3629 | 51.3629 | 40.2025 | 51.3629 | 40.2025 | 73.5542 |  | Snowy Adit 132 kV | 0
Stroud 132 kV | 4.7281 | 4.7284 | 4.7284 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 14.233 | 26.6553 | 14.2929 | 26.544 | 20.4185 | 20.4185 | 18.3516 | 22.491 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 |  | Stroud 132 kV | 1
Sydney East 132 kV | 0.41806 | 0.41808 | 0.41808 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 0.47041 | 0.92777 | 0.48418 | 0.89919 | 0.69168 | 0.69168 | 0.61508 | 0.76995 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 0.69168 | 4.8227 |  | Sydney East 132 kV | 1
Sydney North 132 kV | 0.1392 | 0.13926 | 0.13926 | 0.1185 | 0.1185 | 0.42638 | 0.1185 | 0.1185 | 0.10599 | 0.13654 | 0.08295 | 0.15405 | 0.1185 | 0.1185 | 0.10945 | 0.13685 | 0.1185 | 0.1185 | 0.1185 | 0.1185 | 0.1185 | 0.1185 | 0.1185 | 0.1185 |  | Sydney North 132 kV | 2
Sydney South 132 kV | 0.14955 | 0.14963 | 0.14963 | 0.093211 | 0.093211 | 0.31554 | 0.093211 | 0.093211 | 0.085039 | 0.10675 | 0.065248 | 0.12118 | 0.093211 | 0.093211 | 0.0872 | 0.10812 | 0.093211 | 0.093211 | 0.093211 | 0.093211 | 0.093211 | 0.093211 | 0.093211 | 0.093211 |  | Sydney South 132 kV | 2
Sydney West 132 kV | 0.7075 | 0.70762 | 0.70762 | 0.89013 | 0.89013 | 0.89013 | 0.89013 | 0.13179 | 0.095905 | 0.93146 | 0.62309 | 0.17132 | 0.89013 | 0.89013 | 0.79768 | 0.98335 | 0.89013 | 0.89013 | 0.89013 | 0.89013 | 0.13179 | 0.89013 | 0.13179 | 0.89013 |  | Sydney West 132 kV | 1
Tamworth 66 kV | 3.99 | 3.9903 | 3.9903 | 2.759 | 2.759 | 2.759 | 17.6536 | 2.759 | 2.1464 | 3.5766 | 2.2112 | 3.5867 | 2.759 | 2.759 | 2.7966 | 3.0477 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 17.6536 | 2.759 | 17.6536 |  | Tamworth 66 kV | 1
Taree 33 kV | 12.5373 | 12.5454 | 12.5454 | 31.4802 | 31.4802 | 31.4802 | 31.4802 | 19.4681 | 23.4862 | 39.5409 | 22.0361 | 40.9243 | 31.4802 | 31.4802 | 28.2975 | 34.6708 | 31.4802 | 31.4802 | 31.4802 | 31.4802 | 19.4681 | 31.4802 | 19.4681 | 31.4802 |  | Taree 33 kV | 1
Taree 66 kV | 9.418 | 9.422 | 9.422 | 2.2055 | 2.2055 | 2.2055 | 27.1543 | 2.2055 | 1.6028 | 2.2289 | 1.5438 | 2.8671 | 2.2055 | 2.2055 | 1.9452 | 2.4746 | 2.2055 | 2.2055 | 2.2055 | 2.2055 | 2.2055 | 2.2055 | 2.2055 | 27.1543 |  | Taree 66 kV | 1
Tenterfield 22 kV | 23.2625 | 23.2663 | 23.2663 | 63.3139 | 63.3139 | 63.3139 | 63.3139 | 27.1366 | 44.719 | 58.1321 | 44.3197 | 35.2778 | 27.1366 | 63.3139 | 56.9695 | 29.861 | 63.3139 | 63.3139 | 63.3139 | 63.3139 | 27.1366 | 63.3139 | 27.1366 | 63.3139 |  | Tenterfield 22 kV | 1
Tomago 132 Note 3 | 16.676 | 16.6763 | 16.6763 | 9.5861 | 9.5861 | 9.5861 | 9.5861 | 9.5861 | 6.729 | 12.5335 | 6.7103 | 12.462 | 9.5861 | 9.5861 | 8.553 | 10.6359 | 9.5861 | 9.5861 | 9.5861 | 9.5861 | 9.5861 | 9.5861 | 0.82886 | 9.5861 |  | Tomago 132 Note 3 | 1
Tomago 330 kV | 6.2491 | 6.2543 | 6.2543 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 7.0867 | 12.8924 | 6.9611 | 12.9277 | 9.9444 | 9.9444 | 8.8459 | 11.0662 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 9.9444 | 9.9444 |  | Tomago 330 kV | 1
Tuggerah 132 kV | 4.7281 | 4.7284 | 4.7284 | 11.6609 | 11.6609 | 11.6609 | 11.6609 | 1.7438 | 8.2583 | 15.082 | 8.1626 | 15.1592 | 11.6609 | 11.6609 | 10.4857 | 12.8381 | 11.6609 | 11.6609 | 11.6609 | 11.6609 | 1.9971 | 11.6609 | 1.9971 | 26.3004 |  | Tuggerah 132 kV | 1
Tumut 66 kV | 4.7281 | 4.7284 | 4.7284 | 10.9222 | 10.9222 | 10.9222 | 22.7799 | 4.3327 | 2.9443 | 14.1431 | 7.6456 | 5.6325 | 4.3327 | 10.9222 | 9.8213 | 4.8436 | 10.9222 | 10.9222 | 10.9222 | 10.9222 | 4.3327 | 10.9222 | 4.3327 | 22.7799 |  | Tumut 66 kV | 1
Vales Pt 132 kV | 5.9208 | 5.9248 | 5.9248 | 1.3921 | 1.3921 | 1.3921 | 29.0977 | 1.3921 | 2.6839 | 1.6624 | 20.3684 | 1.8098 | 1.3921 | 29.0977 | 26.1563 | 1.5554 | 29.0977 | 1.3921 | 1.3921 | 1.3921 | 1.3921 | 29.0977 | 1.3921 | 29.0977 |  | Vales Pt 132 kV | 1
Vineyard 132 kV | 3.99 | 3.9903 | 3.9903 | 0.66601 | 0.66601 | 0.66601 | 23.8148 | 0.66601 | 1.0947 | 0.96599 | 16.6704 | 0.86581 | 0.66601 | 23.8148 | 21.4201 | 0.76321 | 23.8148 | 0.66601 | 0.66601 | 0.66601 | 0.66601 | 23.8148 | 0.66601 | 38.2687 |  | Vineyard 132 kV | 1
Wagga 66 kV | 4.015 | 4.0157 | 4.0157 | 26.9133 | 26.9133 | 26.9133 | 26.9133 | 1.2615 | 19.3244 | 32.5757 | 18.8393 | 33.0008 | 26.9133 | 26.9133 | 24.1929 | 29.6405 | 26.9133 | 26.9133 | 26.9133 | 26.9133 | 3.705 | 26.9133 | 3.705 | 26.9133 |  | Wagga 66 kV | 1
Wagga North 132 kV | 4.451 | 5.9859 | 5.9859 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 3.2206 | 5.4712 | 2.9294 | 5.4403 | 4.1848 | 4.1848 | 3.7594 | 4.6119 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 |  | Wagga North 132 kV | 1
Wagga North 66 kV | 16.2658 | 16.2739 | 16.2739 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 24.5146 | 38.816 | 22.1534 | 41.142 | 31.6477 | 31.6477 | 28.4661 | 34.8332 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 31.6477 | 31.6477 |  | Wagga North 66 kV | 0
Wallerawang 132 kV Note 3 | 4.8235 | 4.8255 | 4.8255 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 18.4235 | 32.9051 | 17.9491 | 33.3341 | 25.6416 | 25.6416 | 23.0549 | 28.2336 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 3.6113 | 25.6416 |  | Wallerawang 132 kV Note 3 | 1
Wallerawang 66 kV | 4.7281 | 4.7284 | 4.7284 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 23.5667 | 38.2847 | 21.6222 | 40.1559 | 30.8889 | 30.8889 | 27.7612 | 34.0257 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 |  | Wallerawang 66 kV | 1
Waratah West 132 kV | 4.7281 | 4.7284 | 4.7284 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.7216 | 1.3396 | 2.232 | 1.3802 | 2.5633 | 1.9718 | 1.9718 | 1.7456 | 1.9018 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 22.2263 |  | Waratah West 132 kV | 1
Wellington 132 kV Note 3 | 2.201 | 3.8556 | 3.8556 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 2.649 | 4.8571 | 2.6228 | 4.871 | 3.7469 | 3.7469 | 3.3581 | 4.1389 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 3.7469 | 17.3555 |  | Wellington 132 kV Note 3 | 1
Wellington Town | 9.4526 | 9.4525 | 9.4525 | 68.0114 | 20.353 | 68.0114 | 68.0114 | 21.3512 | 47.608 | 88.4147 | 47.608 | 88.4147 | 68.0114 | 68.0114 | 61.2126 | 74.8102 | 68.0114 | 68.0114 | 68.0114 | 68.0114 | 21.3512 | 68.0114 | 12.5724 | 68.0114 |  | Wellington Town | 0
Williamsdale 132 kV Note 3 | 1.6351 | 1.6352 | 1.6352 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.3249 | 4.1824 | 2.6227 | 4.8708 | 3.7468 | 3.7468 | 3.3642 | 4.1311 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.7468 | 3.7468 |  | Williamsdale 132 kV Note 3 | 1
Yanco 33 kV | 5.9208 | 5.9248 | 5.9248 | 26.6751 | 26.6751 | 26.6751 | 26.6751 | 3.6419 | 4.711 | 32.5003 | 18.6726 | 4.7345 | 3.6419 | 26.6751 | 23.9681 | 4.0361 | 26.6751 | 26.6751 | 26.6751 | 26.6751 | 3.6419 | 26.6751 | 3.6419 | 26.6751 |  | Yanco 33 kV | 1
Yass 132 kV | 14.4688 | 12.1299 | 12.1299 | 17.6257 | 17.6257 | 17.6257 | 34.7614 | 3.3459 | 24.2236 | 4.5417 | 24.3331 | 4.3496 | 17.6257 | 17.6257 | 15.8183 | 19.4433 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 |  | Yass 132 kV | -1
Yass 66 kV | 19.0185 | 19.0205 | 19.0205 | 10.5103 | 10.5103 | 10.5103 | 34.5059 | 10.5103 | 8.3039 | 12.8165 | 7.3572 | 13.6633 | 10.5103 | 10.5103 | 9.4081 | 11.6238 | 10.5103 | 10.5103 | 10.5103 | 10.5103 | 10.5103 | 34.5059 | 10.5103 | 10.5103 |  | Yass 66 kV | 0
|  |  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## summary_MWh_currstd
current std EUE (MWh) | DR | out23_0 | _input0 | basecase | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130 |  | If current std is N-x, | x
Albury 132 kV | 4.1977 | 4.1984 | 4.1984 | 12.1426 | 12.1426 | 20.6949 | 0.69908 | 8.455 | 15.8685 | 8.4998 | 15.7854 | 12.1426 | 12.1426 | 10.9096 | 13.3799 | 12.1426 | 12.1426 | 12.1426 | 12.1426 | 0.69908 | 20.6949 | 0.69908 | 20.6949 | x | Albury 132 kV | 1
ANM 132 kV | 24.997 | 25.0066 | 25.0066 | 6.593 | 6.593 | 8.5365 | 6.593 | 5.5159 | 8.6665 | 5.9756 | 8.5709 | 6.593 | 6.593 | 7.4862 | 7.279 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 |  | ANM 132 kV | 1
Armidale 66 kV | 1.592 | 1.592 | 1.592 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.0522 | 1.2176 | 0.88399 | 1.6417 | 1.2629 | 1.2629 | 1.1188 | 1.4109 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 5.3625 |  | Armidale 66 kV | 1
Balranald 22 kV | 2.4698 | 11.2252 | 11.2252 | 11.3505 | 11.3505 | 11.3505 | 11.3505 | 8.0095 | 14.6914 | 7.9453 | 14.7556 | 11.3505 | 11.3505 | 10.2158 | 12.4851 | 11.3505 | 11.3505 | 11.3505 | 11.3505 | 11.3505 | 11.3505 | 11.3505 | 11.3505 |  | Balranald 22 kV | 0
Beaconsfield 132 kV | 6.5465 | 1.5433 | 1.5433 | 0.5367 | 0.5367 | 0.5367 | 0.5367 | 0.43926 | 0.64193 | 0.37569 | 0.6977 | 0.5367 | 0.5367 | 0.46819 | 0.60787 | 0.5367 | 0.5367 | 0.5367 | 0.5367 | 0.5367 | 0.5367 | 0.5367 | 0.5367 |  | Beaconsfield 132 kV | 2
Beryl 66 kV | 2.6123 | 2.6124 | 2.6124 | 2.088 | 2.088 | 10.6702 | 2.088 | 1.6244 | 2.7068 | 7.4692 | 2.7145 | 2.088 | 10.6702 | 9.5967 | 2.3065 | 10.6702 | 2.088 | 2.088 | 2.088 | 2.088 | 10.6702 | 2.088 | 10.6702 |  | Beryl 66 kV | 1
Boambee South 132 kV | 0.84396 | 0.84402 | 0.84402 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 2.3929 | 4.463 | 2.398 | 4.4534 | 3.4257 | 3.4257 | 3.081 | 3.7708 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 0.74915 | 3.4257 |  | Boambee South 132 kV | 1
Boggabri East | 2.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Boggabri East | -1
Boggabri North | 4.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Boggabri North | -1
Brandy Hill 132 kV | 1.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Brandy Hill 132 kV | -1
Broken Hill 22 kV | 1.5527 | 84.2684 | 84.2684 | 128.9274 | 128.9274 | 128.9274 | 128.9274 | 90.9058 | 166.949 | 90.2492 | 167.6056 | 128.9274 | 128.9274 | 116.0381 | 141.8169 | 128.9274 | 128.9274 | 128.9274 | 128.9274 | 128.9274 | 128.9274 | 128.9274 | 128.9274 |  | Broken Hill 22 kV | 0
Broken Hill 220 kV | 49.266 | 49.266 | 49.266 | 114.3731 | 114.3731 | 114.3731 | 114.3731 | 80.0612 | 148.6851 | 80.0612 | 148.6851 | 114.3731 | 114.3731 | 102.9398 | 125.8065 | 114.3731 | 114.3731 | 114.3731 | 114.3731 | 114.3731 | 114.3731 | 114.3731 | 114.3731 |  | Broken Hill 220 kV | 0
Canberra 132 kV Note 3 | 8.0808 | 8.0811 | 8.0811 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 3.7673 | 6.1581 | 3.4564 | 6.4191 | 4.9378 | 4.9378 | 4.4176 | 5.4638 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 |  | Canberra 132 kV Note 3 | 1
Casino 132 kV | 0.64878 | 30.5113 | 30.5113 | 47.103 | 47.103 | 47.103 | 47.103 | 32.9721 | 61.2339 | 32.9721 | 61.2339 | 47.103 | 47.103 | 42.3943 | 51.8117 | 47.103 | 47.103 | 47.103 | 47.103 | 47.103 | 47.103 | 47.103 | 47.103 |  | Casino 132 kV | 0
Coffs Harbour 66 kV | 2.6914 | 2.6914 | 2.6914 | 1.4543 | 1.4543 | 2.4742 | 0.60435 | 1.8074 | 0.74931 | 1.7319 | 0.78566 | 1.4543 | 1.4543 | 1.2943 | 1.6174 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 |  | Coffs Harbour 66 kV | 1
Coleambally 132 kV | 1.4534 | 1.4536 | 1.4536 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 1.4893 | 2.7734 | 2.3462 | 2.7697 | 2.1305 | 3.3518 | 3.0155 | 2.3446 | 3.3518 | 2.1305 | 2.1305 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 3.3518 |  | Coleambally 132 kV | 1
Cooma 11 kV | 1.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Cooma 11 kV | -1
Cooma 66 kV | 1.7152 | 1.7166 | 1.7166 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.3259 | 2.4156 | 1.3085 | 2.4301 | 1.8693 | 1.8693 | 1.6809 | 2.058 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 |  | Cooma 66 kV | 1
Cooma 132 kV | 6.1492 | 1.6386 | 1.6386 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 2.614 | 4.8831 | 2.6217 | 4.8689 | 3.7453 | 3.7453 | 3.3676 | 4.1237 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 |  | Cooma 132 kV | 1
Cowra 66 kV | 3.197 | 3.1991 | 3.1991 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 3.1239 | 5.2221 | 2.917 | 5.4174 | 4.1672 | 4.1672 | 3.7445 | 4.5913 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 |  | Cowra 66 kV | 1
Dapto 132 kV | 9.1755 | 9.1777 | 9.1777 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 12.9148 | 24.2081 | 12.9501 | 24.0501 | 18.5001 | 18.5001 | 16.5681 | 20.4504 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 |  | Dapto 132 kV | 1
Darlington Point 132 kV Note 3 | 1.9205 | 1.9221 | 1.9221 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.41537 | 0.75886 | 0.41098 | 0.76325 | 0.58712 | 0.58712 | 0.52842 | 0.64581 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 |  | Darlington Point 132 kV Note 3 | 1
Deniliquin 66 kV | 1.9291 | 1.9292 | 1.9292 | 6.985 | 6.985 | 6.985 | 1.418 | 4.9482 | 9.0306 | 4.8895 | 1.8434 | 1.418 | 6.985 | 6.2822 | 1.5852 | 6.985 | 6.985 | 6.985 | 6.985 | 1.418 | 6.985 | 1.418 | 6.985 |  | Deniliquin 66 kV | 1
Dorrigo 132 kV | 0.85493 | 4.2904 | 4.2904 | 4.2311 | 4.2311 | 4.2311 | 4.2311 | 2.9618 | 5.5005 | 2.9618 | 5.5005 | 4.2311 | 4.2311 | 3.8081 | 4.6541 | 4.2311 | 4.2311 | 4.2311 | 4.2311 | 4.2311 | 4.2311 | 4.2311 | 4.2311 |  | Dorrigo 132 kV | 0
Finley 132 kV | 2.4597 | 0.65546 | 0.65546 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.0944 | 3.9066 | 2.099 | 3.8981 | 2.9986 | 2.9986 | 2.6969 | 3.3007 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 0.60964 | 2.9986 |  | Finley 132 kV | 1
Finley 66 kV | 0.80378 | 0.80383 | 0.80383 | 1.5862 | 1.5862 | 5.1027 | 0.38403 | 2.2082 | 2.052 | 3.5719 | 2.0621 | 1.5862 | 1.5862 | 3.2982 | 1.7463 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 0.38403 | 3.6667 | 0.38403 | 3.6667 |  | Finley 66 kV | 1
Forbes 66 kV | 1.3262 | 1.3263 | 1.3263 | 4.771 | 4.771 | 4.771 | 0.93854 | 3.3799 | 6.1681 | 3.3397 | 6.2023 | 4.771 | 4.771 | 4.2909 | 5.2517 | 4.771 | 4.771 | 4.771 | 4.771 | 0.93854 | 4.771 | 0.93854 | 4.771 |  | Forbes 66 kV | 1
Gadara (132 kV & 11 kV) | 17.479 | 17.4801 | 17.4801 | 6.7941 | 6.7941 | 11.487 | 6.7941 | 4.8002 | 8.7992 | 4.7559 | 8.8324 | 6.7941 | 6.7941 | 6.1094 | 7.4802 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 90.2109 |  | Gadara (132 kV & 11 kV) | 1
Glen Innes 66 kV | 1.2788 | 1.2796 | 1.2796 | 2.0923 | 2.0923 | 3.504 | 2.0923 | 1.5084 | 2.6788 | 2.4528 | 2.72 | 2.0923 | 3.504 | 3.1511 | 2.3032 | 3.504 | 2.0923 | 2.0923 | 2.0923 | 1.3116 | 3.504 | 2.0923 | 3.504 |  | Glen Innes 66 kV | 1
Griffith 33 kV | 2.9845 | 2.9847 | 2.9847 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 4.7197 | 8.7227 | 4.7006 | 8.7297 | 6.7152 | 6.7152 | 6.0377 | 7.394 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 1.2732 | 15.1624 |  | Griffith 33 kV | 1
Gunnedah 66 kV | 1.0449 | 1.045 | 1.045 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 2.7448 | 5.0072 | 2.7115 | 5.0357 | 3.8736 | 3.8736 | 3.4839 | 4.2639 | 3.8736 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 3.8736 | 0.69009 | 3.8736 |  | Gunnedah 66 kV | 1
Hawks Nest 132 kV | 1.3308 | 9.0404 | 9.0404 | 10.8151 | 10.8151 | 10.8151 | 10.8151 | 7.5706 | 14.0596 | 7.5706 | 14.0596 | 10.8151 | 10.8151 | 9.734 | 11.8963 | 10.8151 | 10.8151 | 10.8151 | 10.8151 | 10.8151 | 10.8151 | 10.8151 | 10.8151 |  | Hawks Nest 132 kV | 0
Haymarket 132 kV | 8.041 | 1.8957 | 1.8957 | 0.30895 | 1.3908 | 0.30895 | 0.30895 | 0.2469 | 0.37598 | 0.21627 | 0.40164 | 0.30895 | 0.30895 | 0.26954 | 0.34986 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 | 0.30895 |  | Haymarket 132 kV | 2
Herons Creek | 1.6166 | 14.3013 | 14.3013 | 15.4837 | 15.4837 | 15.4837 | 15.4837 | 10.8386 | 20.1288 | 10.8386 | 20.1288 | 15.4837 | 15.4837 | 13.9359 | 17.0316 | 15.4837 | 15.4837 | 15.4837 | 15.4837 | 15.4837 | 15.4837 | 15.4837 | 15.4837 |  | Herons Creek | 0
Holroyd 132 kV | 17.9376 | 17.9397 | 17.9397 | 57.2802 | 57.2802 | 57.2802 | 57.2802 | 41.5083 | 73.1686 | 40.0961 | 74.4643 | 57.2802 | 57.2802 | 51.4474 | 63.0377 | 57.2802 | 57.2802 | 2.0848 | 57.2802 | 48.291 | 57.2802 | 2.0848 | 57.2802 |  | Holroyd 132 kV | 1
Ilford 132 kV | 1.4249 | 7.1506 | 7.1506 | 13.2034 | 13.2034 | 13.2034 | 13.2034 | 9.2424 | 17.1644 | 9.2424 | 17.1644 | 13.2034 | 13.2034 | 11.8835 | 14.5233 | 13.2034 | 13.2034 | 13.2034 | 13.2034 | 13.2034 | 13.2034 | 13.2034 | 13.2034 |  | Ilford 132 kV | 0
Ingleburn 66 kV | 1.8801 | 1.8801 | 1.8801 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 0.59504 | 5.7078 | 3.1837 | 0.78335 | 4.5481 | 4.5481 | 4.0926 | 5.0038 | 4.5481 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 4.5481 | 0.60258 | 4.5481 |  | Ingleburn 66 kV | 1
Inverell 66 kV | 2.8819 | 2.8831 | 2.8831 | 8.6578 | 8.6578 | 8.6578 | 5.3129 | 4.5418 | 10.81 | 6.0605 | 8.0844 | 5.3129 | 8.6578 | 7.7818 | 6.8503 | 8.6578 | 6.2188 | 8.6578 | 8.6578 | 5.3129 | 8.6578 | 5.3129 | 8.6578 |  | Inverell 66 kV | 1
Kempsey 33 kV | 2.2038 | 2.2038 | 2.2038 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 1.2358 | 1.8961 | 1.0909 | 2.026 | 1.5584 | 1.5584 | 1.3949 | 1.7237 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 8.0671 |  | Kempsey 33 kV | 1
Koolkhan 66 kV | 2.6198 | 2.6214 | 2.6214 | 6.3276 | 6.3276 | 7.4603 | 5.3837 | 5.2661 | 6.9772 | 5.2222 | 6.9989 | 6.3276 | 6.3276 | 5.6861 | 6.9711 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 0.3358 | 6.3276 |  | Koolkhan 66 kV | 1
Liddell 330 kV (33 kV supply via Mac Gen) | 2.0474 | 2.0474 | 2.0474 | 0.28796 | 0.28796 | 1.8246 | 0.28796 | 1.2232 | 0.38478 | 1.2772 | 0.37435 | 0.28796 | 0.49095 | 0.4212 | 0.31969 | 0.49095 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 |  | Liddell 330 kV (33 kV supply via Mac Gen) | 1
Lismore 132 kV Note 3 | 4.264 | 4.2657 | 4.2657 | 2.4687 | 2.4687 | 17.2288 | 2.4687 | 1.9206 | 3.2003 | 1.9786 | 3.2093 | 2.4687 | 2.8266 | 2.5024 | 2.727 | 2.8266 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 17.2288 |  | Lismore 132 kV Note 3 | 1
Liverpool 132 kV | 2.8851 | 2.8851 | 2.8851 | 7.6165 | 7.6165 | 20.6133 | 0.86207 | 5.3622 | 7.2639 | 5.3316 | 7.2763 | 5.5972 | 7.6165 | 6.8502 | 6.1626 | 7.6165 | 5.5972 | 7.6165 | 7.6165 | 0.86207 | 7.6165 | 0.86207 | 18.8598 |  | Liverpool 132 kV | 1
Macarthur 132 kV | 1.9759 | 1.9759 | 1.9759 | 3.6496 | 3.6496 | 7.4825 | 0.7577 | 0.54092 | 7.7675 | 2.5547 | 0.98501 | 3.6496 | 3.6496 | 3.2623 | 4.0417 | 7.4825 | 3.6496 | 3.6496 | 3.6496 | 0.7577 | 7.4825 | 0.7577 | 14.3023 |  | Macarthur 132 kV | 1
Macarthur 66 kV | 0.43366 | 0.43366 | 0.43366 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.42454 | 0.75795 | 0.41387 | 0.76862 | 0.59124 | 0.59124 | 0.53214 | 0.65035 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 5.8942 |  | Macarthur 66 kV | 1
Macksville 132 kV | 1.7796 | 1.7799 | 1.7799 | 1.6928 | 1.6928 | 2.8782 | 0.79952 | 2.0125 | 2.2046 | 2.0147 | 2.2006 | 1.6928 | 1.6928 | 2.5895 | 1.8631 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 0.79952 | 1.6928 | 0.79952 | 1.6928 |  | Macksville 132 kV | 1
Manildra 132 kV | 1.118 | 1.1181 | 1.1181 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.45925 | 0.93157 | 0.48043 | 0.89223 | 0.68633 | 0.68633 | 0.60865 | 0.76603 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 |  | Manildra 132 kV | 1
Marulan 132 kV | 7.2336 | 14.7056 | 14.7056 | 79.021 | 79.021 | 79.021 | 79.021 | 57.5509 | 100.7519 | 55.3147 | 102.7274 | 79.021 | 79.021 | 70.991 | 87.08 | 79.021 | 79.021 | 79.021 | 79.021 | 79.021 | 79.021 | 79.021 | 79.021 |  | Marulan 132 kV | 0
Molong 66 kV | 0.6913 | 2.4809 | 2.4809 | 4.884 | 4.884 | 4.884 | 4.884 | 3.4953 | 6.2787 | 3.4188 | 6.3492 | 4.884 | 4.884 | 4.3927 | 5.3759 | 4.884 | 4.884 | 4.884 | 4.884 | 4.884 | 4.884 | 4.884 | 4.884 |  | Molong 66 kV | 0
Moree 66 kV | 1.5674 | 1.5675 | 1.5675 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.5604 | 1.1102 | 0.57729 | 1.0721 | 0.8247 | 0.8247 | 0.73013 | 0.92197 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 |  | Moree 66 kV | 1
Morven 132 kV | 1.3308 | 9.0404 | 9.0404 | 11.3671 | 11.3671 | 11.3671 | 11.3671 | 7.957 | 14.7773 | 7.957 | 14.7773 | 11.3671 | 11.3671 | 10.2308 | 12.5034 | 11.3671 | 11.3671 | 11.3671 | 11.3671 | 11.3671 | 11.3671 | 11.3671 | 11.3671 |  | Morven 132 kV | 0
Mount Piper 66 kV | 3.3622 | 3.3637 | 3.3637 | 5.851 | 5.851 | 5.851 | 0.57173 | 4.4461 | 7.2713 | 4.0957 | 7.6063 | 5.851 | 5.851 | 5.2578 | 6.446 | 5.851 | 5.851 | 5.851 | 5.851 | 0.57173 | 5.851 | 0.57173 | 5.851 |  | Mount Piper 66 kV | 1
Mudgee 132 kV | 0.52864 | 24.8611 | 24.8611 | 34.713 | 34.713 | 34.713 | 34.713 | 24.2991 | 45.1269 | 24.2991 | 45.1269 | 34.713 | 34.713 | 31.2429 | 38.1831 | 34.713 | 34.713 | 34.713 | 34.713 | 34.713 | 34.713 | 34.713 | 34.713 |  | Mudgee 132 kV | 0
Munmorah 132 kV | 11.1424 | 11.1427 | 11.1427 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 3.0801 | 17.2023 | 10.1373 | 4.5933 | 3.5333 | 14.4819 | 13.0268 | 3.9088 | 14.4819 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 14.4819 | 3.5333 | 26.5934 |  | Munmorah 132 kV | 1
Munmorah 330 kV (via old Power Stn Txs) | 4.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Munmorah 330 kV (via old Power Stn Txs) | -1
Munyang 33 kV | 3.1221 | 19.9958 | 19.9958 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 0.89834 | 1.6461 | 0.89054 | 1.6539 | 1.2722 | 1.2722 | 1.145 | 1.3994 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 1.2722 |  | Munyang 33 kV | 0
Murrumbateman 132 kV | 0.9981 | 6.7803 | 6.7803 | 6.8747 | 6.8747 | 6.8747 | 6.8747 | 4.8123 | 8.9372 | 4.8123 | 8.9372 | 6.8747 | 6.8747 | 6.1875 | 7.562 | 6.8747 | 6.8747 | 6.8747 | 6.8747 | 6.8747 | 6.8747 | 6.8747 | 6.8747 |  | Murrumbateman 132 kV | 0
Murrumburrah 66 kV | 1.6076 | 1.6077 | 1.6077 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 3.8977 | 7.1127 | 3.8512 | 7.1522 | 5.5017 | 5.5017 | 4.9482 | 6.056 | 5.5017 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 5.5017 | 1.0847 | 5.5017 |  | Murrumburrah 66 kV | 1
Muswellbrook 132 kV | 9.8864 | 9.8871 | 9.8871 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 3.1683 | 5.2791 | 2.8505 | 5.2938 | 4.0722 | 4.0722 | 3.6496 | 4.4982 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 |  | Muswellbrook 132 kV | 1
Nambucca 66 kV | 1.7796 | 1.7799 | 1.7799 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 1.7671 | 3.2329 | 1.7495 | 3.2491 | 2.4993 | 2.4993 | 2.2487 | 2.75 | 2.4993 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 2.4993 | 1.6852 | 2.4993 |  | Nambucca 66 kV | 1
Narrabri 66 kV | 0.91398 | 0.91415 | 0.91415 | 1.1622 | 1.1622 | 6.0966 | 0.95635 | 0.84345 | 1.1749 | 0.81351 | 1.2433 | 1.1622 | 1.1622 | 1.025 | 1.055 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 6.0966 |  | Narrabri 66 kV | 1
Newcastle 132 kV | 0.99829 | 0.99869 | 0.99869 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.3921 | 3.0478 | 1.8983 | 3.5255 | 2.7119 | 2.7119 | 2.4313 | 2.9947 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 |  | Newcastle 132 kV | 1
Orange North 132 kV | 7.208 | 2.7236 | 2.7236 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 5.4891 | 10.0096 | 5.4157 | 10.0578 | 7.7367 | 7.7367 | 6.9316 | 8.5489 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 |  | Orange North 132 kV | 1
Orange 66 kV | 1.2765 | 1.2765 | 1.2765 | 1.0615 | 1.0615 | 1.0615 | 0.82782 | 0.81341 | 0.9622 | 0.74308 | 1.0762 | 0.82782 | 1.0615 | 0.93129 | 0.91436 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 |  | Orange 66 kV | 1
Panorama 66 kV | 2.974 | 2.9742 | 2.9742 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 1.5192 | 2.5315 | 1.5649 | 2.5387 | 1.9529 | 2.2356 | 1.9793 | 2.1572 | 2.2356 | 1.9529 | 1.9529 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 6.0093 |  | Panorama 66 kV | 1
Parkes 132 kV | 4.0585 | 0.66894 | 0.66894 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 2.1652 | 4.6908 | 2.3455 | 4.3559 | 3.3507 | 3.3507 | 2.9385 | 3.7801 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 |  | Parkes 132 kV | 1
Parkes 66 kV | 2.6642 | 2.6659 | 2.6659 | 8.2898 | 8.2898 | 8.2898 | 0.87157 | 6.0838 | 10.5107 | 5.8029 | 10.7768 | 8.2898 | 8.2898 | 7.4533 | 9.1281 | 8.2898 | 8.2898 | 8.2898 | 8.2898 | 1.5996 | 8.2898 | 1.5996 | 8.2898 |  | Parkes 66 kV | 1
Port Macquarie 33 kV | 2.2524 | 2.2528 | 2.2528 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 4.516 | 8.2914 | 4.4748 | 8.3102 | 6.3925 | 6.3925 | 5.742 | 7.0455 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 0.60157 | 6.3925 |  | Port Macquarie 33 kV | 1
Queanbeyan 66 kV | 3.9991 | 3.9995 | 3.9995 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 0.85001 | 1.5622 | 5.0273 | 1.5679 | 1.2061 | 7.1819 | 6.441 | 1.3267 | 7.1819 | 1.2061 | 1.2061 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 7.1819 |  | Queanbeyan 66 kV | 1
Raleigh 132 kV | 1.9773 | 1.9776 | 1.9776 | 1.8918 | 1.8918 | 2.899 | 1.8918 | 2.0276 | 2.4624 | 2.0293 | 2.4594 | 1.8918 | 1.8918 | 1.702 | 2.0818 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 |  | Raleigh 132 kV | 1
Regentville 132 kV | 11.3734 | 11.3742 | 11.3742 | 19.7476 | 19.7476 | 31.5849 | 19.7476 | 13.9977 | 25.531 | 22.1094 | 25.6719 | 19.7476 | 19.7476 | 17.7564 | 21.7425 | 19.7476 | 19.7476 | 19.7476 | 19.7476 | 1.4236 | 31.5849 | 1.4236 | 31.5849 |  | Regentville 132 kV | 1
Rookwood Road 132 kV | 5.3888 | 1.2704 | 1.2704 | 0.19398 | 1.9485 | 0.19398 | 0.19398 | 0.81102 | 0.23606 | 0.61125 | 0.25217 | 0.19398 | 0.19398 | 0.16923 | 0.21966 | 0.19398 | 0.19398 | 0.19398 | 0.19398 | 0.19398 | 0.19398 | 0.19398 | 0.19398 |  | Rookwood Road 132 kV | 2
Snowy Adit 132 kV | 1.6166 | 14.3013 | 14.3013 | 10.6592 | 10.6592 | 10.6592 | 10.6592 | 7.4614 | 13.8569 | 7.4614 | 13.8569 | 10.6592 | 10.6592 | 9.5936 | 11.7247 | 10.6592 | 10.6592 | 10.6592 | 10.6592 | 10.6592 | 10.6592 | 10.6592 | 10.6592 |  | Snowy Adit 132 kV | 0
Stroud 132 kV | 1.2057 | 1.2057 | 1.2057 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 2.9842 | 5.5887 | 2.9968 | 5.5654 | 4.2811 | 4.2811 | 3.8477 | 4.7156 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 |  | Stroud 132 kV | 1
Sydney East 132 kV | 2.459 | 2.4591 | 2.4591 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 2.1726 | 4.2849 | 2.2362 | 4.1529 | 3.1945 | 3.1945 | 2.8407 | 3.556 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 22.2734 |  | Sydney East 132 kV | 1
Sydney North 132 kV | 1.085 | 1.085 | 1.085 | 0.85741 | 3.0843 | 0.85741 | 0.85741 | 0.76687 | 0.98788 | 0.60019 | 1.1146 | 0.85741 | 0.85741 | 0.79186 | 0.99022 | 0.85741 | 0.85741 | 0.85741 | 0.85741 | 0.85741 | 0.85741 | 0.85741 | 0.85741 |  | Sydney North 132 kV | 2
Sydney South 132 kV | 1.1822 | 1.1822 | 1.1822 | 0.85006 | 2.8766 | 0.85006 | 0.85006 | 0.77552 | 0.97344 | 0.59504 | 1.1051 | 0.85006 | 0.85006 | 0.79518 | 0.98606 | 0.85006 | 0.85006 | 0.85006 | 0.85006 | 0.85006 | 0.85006 | 0.85006 | 0.85006 |  | Sydney South 132 kV | 2
Sydney West 132 kV | 7.5954 | 7.5967 | 7.5967 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 0.81424 | 7.9082 | 5.2901 | 1.4545 | 7.5573 | 7.5573 | 6.7724 | 8.3487 | 7.5573 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 7.5573 | 1.1189 | 7.5573 |  | Sydney West 132 kV | 1
Tamworth 66 kV | 3.968 | 3.9683 | 3.9683 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 1.8863 | 3.1432 | 1.9432 | 3.152 | 2.4246 | 2.4246 | 2.4577 | 2.6783 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 15.514 |  | Tamworth 66 kV | 1
Taree 33 kV | 2.5576 | 2.5593 | 2.5593 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 4.4154 | 7.4337 | 4.1428 | 7.6938 | 5.9183 | 5.9183 | 5.3199 | 6.5181 | 5.9183 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 5.9183 | 3.66 | 5.9183 |  | Taree 33 kV | 1
Taree 66 kV | 3.9226 | 3.9243 | 3.9243 | 0.91564 | 0.91564 | 11.2735 | 0.91564 | 0.66544 | 0.92535 | 0.64095 | 1.1903 | 0.91564 | 0.91564 | 0.80757 | 1.0274 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 11.2735 |  | Taree 66 kV | 1
Tenterfield 22 kV | 1.1864 | 1.1866 | 1.1866 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.0817 | 2.706 | 2.0631 | 1.6422 | 1.2632 | 2.9473 | 2.6519 | 1.39 | 2.9473 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.9473 | 1.2632 | 2.9473 |  | Tenterfield 22 kV | 1
Tomago 132 Note 3 | 32.4598 | 32.4604 | 32.4604 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 22.8124 | 42.4903 | 22.7489 | 42.2479 | 32.4984 | 32.4984 | 28.996 | 36.0571 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 2.81 | 32.4984 |  | Tomago 132 Note 3 | 1
Tomago 330 kV | 49.93 | 49.9721 | 49.9721 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 110.593 | 201.1949 | 108.6327 | 201.7464 | 155.1895 | 155.1895 | 138.0461 | 172.695 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 |  | Tomago 330 kV | 1
Tuggerah 132 kV | 8.0779 | 8.0785 | 8.0785 | 15.2431 | 15.2431 | 15.2431 | 2.2795 | 10.7952 | 19.7152 | 10.6702 | 19.8161 | 15.2431 | 15.2431 | 13.707 | 16.782 | 15.2431 | 15.2431 | 15.2431 | 15.2431 | 2.6107 | 15.2431 | 2.6107 | 34.3799 |  | Tuggerah 132 kV | 1
Tumut 66 kV | 1.5272 | 1.5273 | 1.5273 | 3.4583 | 3.4583 | 7.2129 | 1.3719 | 0.93225 | 4.4782 | 2.4208 | 1.7834 | 1.3719 | 3.4583 | 3.1098 | 1.5337 | 3.4583 | 3.4583 | 3.4583 | 3.4583 | 1.3719 | 3.4583 | 1.3719 | 7.2129 |  | Tumut 66 kV | 1
Vales Pt 132 kV | 4.2778 | 4.2806 | 4.2806 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 1.6369 | 1.0139 | 12.4223 | 1.1038 | 0.84904 | 17.7462 | 15.9523 | 0.94859 | 17.7462 | 0.84904 | 0.84904 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 17.7462 |  | Vales Pt 132 kV | 1
Vineyard 132 kV | 16.8556 | 16.8569 | 16.8569 | 1.683 | 1.683 | 60.1784 | 1.683 | 2.7664 | 2.441 | 42.1249 | 2.1879 | 1.683 | 60.1784 | 54.1271 | 1.9286 | 60.1784 | 1.683 | 1.683 | 1.683 | 1.683 | 60.1784 | 1.683 | 96.7024 |  | Vineyard 132 kV | 1
Wagga 66 kV | 3.2763 | 3.2768 | 3.2768 | 12.3577 | 12.3577 | 12.3577 | 0.57925 | 8.8731 | 14.9577 | 8.6504 | 15.1529 | 12.3577 | 12.3577 | 11.1086 | 13.6099 | 12.3577 | 12.3577 | 12.3577 | 12.3577 | 1.7012 | 12.3577 | 1.7012 | 12.3577 |  | Wagga 66 kV | 1
Wagga North 132 kV | 2.27 | 3.0528 | 3.0528 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.1238 | 3.6079 | 1.9317 | 3.5875 | 2.7596 | 2.7596 | 2.4791 | 3.0412 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 |  | Wagga North 132 kV | 1
Wagga North 66 kV | 3.733 | 13.3967 | 13.3967 | 10.5879 | 10.5879 | 10.5879 | 10.5879 | 7.7067 | 13.4826 | 7.4116 | 13.7643 | 10.5879 | 10.5879 | 9.5227 | 11.6546 | 10.5879 | 10.5879 | 10.5879 | 10.5879 | 10.5879 | 10.5879 | 10.5879 | 10.5879 |  | Wagga North 66 kV | 0
Wallerawang 132 kV Note 3 | 4.551 | 4.5529 | 4.5529 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 8.5331 | 15.2405 | 8.3134 | 15.4392 | 11.8764 | 11.8764 | 10.6783 | 13.0769 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 1.6726 | 11.8764 |  | Wallerawang 132 kV Note 3 | 1
Wallerawang 66 kV | 1.2057 | 1.2057 | 1.2057 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.64612 | 1.0496 | 0.59281 | 1.1009 | 0.84687 | 0.84687 | 0.76112 | 0.93287 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 |  | Wallerawang 66 kV | 1
Waratah West 132 kV | 6.2694 | 6.2699 | 6.2699 | 2.5513 | 2.5513 | 2.5513 | 2.2276 | 1.7333 | 2.8879 | 1.7859 | 3.3166 | 2.5513 | 2.5513 | 2.2586 | 2.4607 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 28.7586 |  | Waratah West 132 kV | 1
Wellington 132 kV Note 3 | 3.2553 | 5.7025 | 5.7025 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 4.1296 | 7.572 | 4.0889 | 7.5936 | 5.8412 | 5.8412 | 5.2351 | 6.4523 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 27.0563 |  | Wellington 132 kV Note 3 | 1
Wellington Town | 0.96416 | 13.5606 | 13.5606 | 4.9908 | 4.9908 | 4.9908 | 4.9908 | 3.4935 | 6.488 | 3.4935 | 6.488 | 4.9908 | 4.9908 | 4.4919 | 5.4897 | 4.9908 | 4.9908 | 4.9908 | 4.9908 | 4.9908 | 4.9908 | 4.9908 | 4.9908 |  | Wellington Town | 0
Williamsdale 132 kV Note 3 | 2.5851 | 2.5853 | 2.5853 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 5.4861 | 6.901 | 4.3275 | 8.0368 | 6.1822 | 6.1822 | 5.5509 | 6.8163 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 |  | Williamsdale 132 kV Note 3 | 1
Yanco 33 kV | 1.9124 | 1.9137 | 1.9137 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 1.5647 | 10.7944 | 6.2018 | 1.5725 | 1.2096 | 8.8597 | 7.9606 | 1.3405 | 8.8597 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 8.8597 | 1.2096 | 8.8597 |  | Yanco 33 kV | 1
Yass 132 kV | 1.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Yass 132 kV | -1
Yass 66 kV | 2.1015 | 18.5916 | 18.5916 | 6.2109 | 6.2109 | 6.2109 | 6.2109 | 4.591 | 7.8487 | 4.3476 | 8.0742 | 6.2109 | 6.2109 | 5.5807 | 6.8432 | 6.2109 | 6.2109 | 6.2109 | 6.2109 | 6.2109 | 6.2109 | 6.2109 | 6.2109 |  | Yass 66 kV | 0
|  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## summary_MWh_N-1
N-1 EUE (MWh) | DR | out23_0 | _input0 | basecase | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130
Albury 132 kV | 4.1977 | 4.1984 | 4.1984 | 12.1426 | 12.1426 | 20.6949 | 0.69908 | 8.455 | 15.8685 | 8.4998 | 15.7854 | 12.1426 | 12.1426 | 10.9096 | 13.3799 | 12.1426 | 12.1426 | 12.1426 | 12.1426 | 0.69908 | 20.6949 | 0.69908 | 20.6949 | x
ANM 132 kV | 24.997 | 25.0066 | 25.0066 | 6.593 | 6.593 | 8.5365 | 6.593 | 5.5159 | 8.6665 | 5.9756 | 8.5709 | 6.593 | 6.593 | 7.4862 | 7.279 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593 | 6.593
Armidale 66 kV | 1.592 | 1.592 | 1.592 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.0522 | 1.2176 | 0.88399 | 1.6417 | 1.2629 | 1.2629 | 1.1188 | 1.4109 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 1.2629 | 5.3625
Balranald 22 kV | 2.4698 | 2.4703 | 2.4703 | 2.8048 | 2.8048 | 11.3505 | 2.8048 | 1.9747 | 3.6349 | 7.9453 | 3.6463 | 2.8048 | 11.3505 | 10.2158 | 3.0852 | 2.8048 | 2.8048 | 2.8048 | 2.8048 | 2.8048 | 11.3505 | 2.8048 | 11.3505
Beaconsfield 132 kV | 6.5465 | 6.547 | 6.547 | 0.27224 | 6.9859 | 0.27224 | 0.27224 | 0.22815 | 0.31632 | 3.9466 | 0.35391 | 0.27224 | 5.638 | 5.0694 | 0.2995 | 5.638 | 0.27224 | 0.27224 | 5.638 | 0.27224 | 5.638 | 0.27224 | 5.638
Beryl 66 kV | 2.6123 | 2.6124 | 2.6124 | 2.088 | 2.088 | 10.6702 | 2.088 | 1.6244 | 2.7068 | 7.4692 | 2.7145 | 2.088 | 10.6702 | 9.5967 | 2.3065 | 10.6702 | 2.088 | 2.088 | 2.088 | 2.088 | 10.6702 | 2.088 | 10.6702
Boambee South 132 kV | 0.84396 | 0.84402 | 0.84402 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 2.3929 | 4.463 | 2.398 | 4.4534 | 3.4257 | 3.4257 | 3.081 | 3.7708 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 3.4257 | 0.74915 | 3.4257
Boggabri East | 2.632 | 2.6323 | 2.6323 | 7.5519 | 7.5519 | 23.2903 | 7.5519 | 5.3498 | 9.7579 | 16.3032 | 9.8175 | 7.5519 | 23.2903 | 20.9555 | 8.3093 | 7.5519 | 7.5519 | 7.5519 | 7.5519 | 7.5519 | 23.2903 | 7.5519 | 23.2903
Boggabri North | 4.9351 | 4.9356 | 4.9356 | 14.1599 | 14.1599 | 27.5951 | 14.1599 | 10.0309 | 18.2961 | 9.9119 | 18.4078 | 14.1599 | 14.1599 | 12.7406 | 15.58 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 14.1599 | 27.5951
Brandy Hill 132 kV | 1.118 | 1.1181 | 1.1181 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.58058 | 1.15 | 0.59804 | 1.1106 | 0.85434 | 0.85434 | 0.75639 | 0.95509 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434 | 0.85434
Broken Hill 22 kV | 1.5527 | 1.5527 | 1.5527 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 2.804 | 5.1514 | 8.2922 | 5.171 | 3.9777 | 11.846 | 10.6412 | 4.3817 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 11.846
Broken Hill 220 kV | 49.266 | 0.93246 | 0.93246 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 0.83397 | 1.5488 | 0.83397 | 1.5488 | 1.1914 | 1.1914 | 1.0723 | 1.3105 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914
Canberra 132 kV Note 3 | 8.0808 | 8.0811 | 8.0811 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 3.7673 | 6.1581 | 3.4564 | 6.4191 | 4.9378 | 4.9378 | 4.4176 | 5.4638 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378
Casino 132 kV | 0.64878 | 0.64878 | 0.64878 | 1.4112 | 1.4112 | 3.4388 | 1.4112 | 0.98784 | 1.8345 | 2.4071 | 1.8345 | 1.4112 | 1.4112 | 3.095 | 1.5523 | 1.4112 | 1.4112 | 1.4112 | 1.4112 | 1.4112 | 3.4388 | 1.4112 | 3.4388
Coffs Harbour 66 kV | 2.6914 | 2.6914 | 2.6914 | 1.4543 | 1.4543 | 2.4742 | 0.60435 | 1.8074 | 0.74931 | 1.7319 | 0.78566 | 1.4543 | 1.4543 | 1.2943 | 1.6174 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543 | 1.4543
Coleambally 132 kV | 1.4534 | 1.4536 | 1.4536 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 1.4893 | 2.7734 | 2.3462 | 2.7697 | 2.1305 | 3.3518 | 3.0155 | 2.3446 | 3.3518 | 2.1305 | 2.1305 | 2.1305 | 2.1305 | 3.3518 | 2.1305 | 3.3518
Cooma 11 kV | 1.0618 | 1.0627 | 1.0627 | 2.5577 | 2.5577 | 3.6976 | 0.28407 | 2.6074 | 2.0821 | 2.5883 | 2.0901 | 2.5577 | 2.5577 | 2.2999 | 2.816 | 2.5577 | 2.5577 | 2.5577 | 2.5577 | 1.3079 | 2.5577 | 1.3079 | 2.5577
Cooma 66 kV | 1.7152 | 1.7166 | 1.7166 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.3259 | 2.4156 | 1.3085 | 2.4301 | 1.8693 | 1.8693 | 1.6809 | 2.058 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693 | 1.8693
Cooma 132 kV | 6.1492 | 1.6386 | 1.6386 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 2.614 | 4.8831 | 2.6217 | 4.8689 | 3.7453 | 3.7453 | 3.3676 | 4.1237 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.7453
Cowra 66 kV | 3.197 | 3.1991 | 3.1991 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 3.1239 | 5.2221 | 2.917 | 5.4174 | 4.1672 | 4.1672 | 3.7445 | 4.5913 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672 | 4.1672
Dapto 132 kV | 9.1755 | 9.1777 | 9.1777 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 12.9148 | 24.2081 | 12.9501 | 24.0501 | 18.5001 | 18.5001 | 16.5681 | 20.4504 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001 | 18.5001
Darlington Point 132 kV Note 3 | 1.9205 | 1.9221 | 1.9221 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.41537 | 0.75886 | 0.41098 | 0.76325 | 0.58712 | 0.58712 | 0.52842 | 0.64581 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712 | 0.58712
Deniliquin 66 kV | 1.9291 | 1.9292 | 1.9292 | 6.985 | 6.985 | 6.985 | 1.418 | 4.9482 | 9.0306 | 4.8895 | 1.8434 | 1.418 | 6.985 | 6.2822 | 1.5852 | 6.985 | 6.985 | 6.985 | 6.985 | 1.418 | 6.985 | 1.418 | 6.985
Dorrigo 132 kV | 0.85493 | 0.85522 | 0.85522 | 0.83304 | 0.83304 | 4.2311 | 0.72302 | 0.50612 | 1.083 | 0.50612 | 1.083 | 0.83304 | 0.83304 | 0.74977 | 0.91632 | 0.83304 | 0.83304 | 0.83304 | 0.83304 | 0.72302 | 0.83304 | 0.72302 | 0.83304
Finley 132 kV | 2.4597 | 0.65546 | 0.65546 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.0944 | 3.9066 | 2.099 | 3.8981 | 2.9986 | 2.9986 | 2.6969 | 3.3007 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 0.60964 | 2.9986
Finley 66 kV | 0.80378 | 0.80383 | 0.80383 | 1.5862 | 1.5862 | 5.1027 | 0.38403 | 2.2082 | 2.052 | 3.5719 | 2.0621 | 1.5862 | 1.5862 | 3.2982 | 1.7463 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 0.38403 | 3.6667 | 0.38403 | 3.6667
Forbes 66 kV | 1.3262 | 1.3263 | 1.3263 | 4.771 | 4.771 | 4.771 | 0.93854 | 3.3799 | 6.1681 | 3.3397 | 6.2023 | 4.771 | 4.771 | 4.2909 | 5.2517 | 4.771 | 4.771 | 4.771 | 4.771 | 0.93854 | 4.771 | 0.93854 | 4.771
Gadara (132 kV & 11 kV) | 17.479 | 17.4801 | 17.4801 | 6.7941 | 6.7941 | 11.487 | 6.7941 | 4.8002 | 8.7992 | 4.7559 | 8.8324 | 6.7941 | 6.7941 | 6.1094 | 7.4802 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 6.7941 | 90.2109
Glen Innes 66 kV | 1.2788 | 1.2796 | 1.2796 | 2.0923 | 2.0923 | 3.504 | 2.0923 | 1.5084 | 2.6788 | 2.4528 | 2.72 | 2.0923 | 3.504 | 3.1511 | 2.3032 | 3.504 | 2.0923 | 2.0923 | 2.0923 | 1.3116 | 3.504 | 2.0923 | 3.504
Griffith 33 kV | 2.9845 | 2.9847 | 2.9847 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 4.7197 | 8.7227 | 4.7006 | 8.7297 | 6.7152 | 6.7152 | 6.0377 | 7.394 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 6.7152 | 1.2732 | 15.1624
Gunnedah 66 kV | 1.0449 | 1.045 | 1.045 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 2.7448 | 5.0072 | 2.7115 | 5.0357 | 3.8736 | 3.8736 | 3.4839 | 4.2639 | 3.8736 | 3.8736 | 3.8736 | 3.8736 | 0.69009 | 3.8736 | 0.69009 | 3.8736
Hawks Nest 132 kV | 1.3308 | 1.3308 | 1.3308 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 1.5077 | 2.8 | 1.5077 | 2.8 | 2.1538 | 2.1538 | 1.9385 | 2.3691 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 1.8424
Haymarket 132 kV | 8.041 | 8.0417 | 8.0417 | 0.21612 | 9.1753 | 0.21612 | 0.21612 | 0.16862 | 0.26361 | 4.7839 | 0.28095 | 0.21612 | 0.21612 | 0.19424 | 0.23776 | 0.21612 | 0.21612 | 0.21612 | 6.8341 | 0.21612 | 6.8341 | 0.21612 | 23.4343
Herons Creek | 1.6166 | 1.6167 | 1.6167 | 1.2412 | 1.2412 | 2.9524 | 0.45 | 2.0667 | 0.585 | 2.0667 | 0.585 | 1.2412 | 2.0573 | 1.8517 | 1.3653 | 2.0573 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 2.0573 | 1.2412 | 2.0573
Holroyd 132 kV | 17.9376 | 17.9397 | 17.9397 | 57.2802 | 57.2802 | 57.2802 | 57.2802 | 41.5083 | 73.1686 | 40.0961 | 74.4643 | 57.2802 | 57.2802 | 51.4474 | 63.0377 | 57.2802 | 57.2802 | 2.0848 | 57.2802 | 48.291 | 57.2802 | 2.0848 | 57.2802
Ilford 132 kV | 1.4249 | 1.4254 | 1.4254 | 0.82521 | 0.82521 | 2.1133 | 0.82521 | 1.1553 | 1.0728 | 1.1553 | 1.0728 | 0.82521 | 2.1133 | 1.9021 | 0.9077 | 1.6504 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 2.1133 | 0.82521 | 2.1133
Ingleburn 66 kV | 1.8801 | 1.8801 | 1.8801 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 0.59504 | 5.7078 | 3.1837 | 0.78335 | 4.5481 | 4.5481 | 4.0926 | 5.0038 | 4.5481 | 4.5481 | 4.5481 | 4.5481 | 0.60258 | 4.5481 | 0.60258 | 4.5481
Inverell 66 kV | 2.8819 | 2.8831 | 2.8831 | 8.6578 | 8.6578 | 8.6578 | 5.3129 | 4.5418 | 10.81 | 6.0605 | 8.0844 | 5.3129 | 8.6578 | 7.7818 | 6.8503 | 8.6578 | 6.2188 | 8.6578 | 8.6578 | 5.3129 | 8.6578 | 5.3129 | 8.6578
Kempsey 33 kV | 2.2038 | 2.2038 | 2.2038 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 1.2358 | 1.8961 | 1.0909 | 2.026 | 1.5584 | 1.5584 | 1.3949 | 1.7237 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 1.5584 | 8.0671 | 1.5584 | 8.0671
Koolkhan 66 kV | 2.6198 | 2.6214 | 2.6214 | 6.3276 | 6.3276 | 7.4603 | 5.3837 | 5.2661 | 6.9772 | 5.2222 | 6.9989 | 6.3276 | 6.3276 | 5.6861 | 6.9711 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 6.3276 | 0.3358 | 6.3276
Liddell 330 kV (33 kV supply via Mac Gen) | 2.0474 | 2.0474 | 2.0474 | 0.28796 | 0.28796 | 1.8246 | 0.28796 | 1.2232 | 0.38478 | 1.2772 | 0.37435 | 0.28796 | 0.49095 | 0.4212 | 0.31969 | 0.49095 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796 | 0.28796
Lismore 132 kV Note 3 | 4.264 | 4.2657 | 4.2657 | 2.4687 | 2.4687 | 17.2288 | 2.4687 | 1.9206 | 3.2003 | 1.9786 | 3.2093 | 2.4687 | 2.8266 | 2.5024 | 2.727 | 2.8266 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 2.4687 | 17.2288
Liverpool 132 kV | 2.8851 | 2.8851 | 2.8851 | 7.6165 | 7.6165 | 20.6133 | 0.86207 | 5.3622 | 7.2639 | 5.3316 | 7.2763 | 5.5972 | 7.6165 | 6.8502 | 6.1626 | 7.6165 | 5.5972 | 7.6165 | 7.6165 | 0.86207 | 7.6165 | 0.86207 | 18.8598
Macarthur 132 kV | 1.9759 | 1.9759 | 1.9759 | 3.6496 | 3.6496 | 7.4825 | 0.7577 | 0.54092 | 7.7675 | 2.5547 | 0.98501 | 3.6496 | 3.6496 | 3.2623 | 4.0417 | 7.4825 | 3.6496 | 3.6496 | 3.6496 | 0.7577 | 7.4825 | 0.7577 | 14.3023
Macarthur 66 kV | 0.43366 | 0.43366 | 0.43366 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.42454 | 0.75795 | 0.41387 | 0.76862 | 0.59124 | 0.59124 | 0.53214 | 0.65035 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 5.8942
Macksville 132 kV | 1.7796 | 1.7799 | 1.7799 | 1.6928 | 1.6928 | 2.8782 | 0.79952 | 2.0125 | 2.2046 | 2.0147 | 2.2006 | 1.6928 | 1.6928 | 2.5895 | 1.8631 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 0.79952 | 1.6928 | 0.79952 | 1.6928
Manildra 132 kV | 1.118 | 1.1181 | 1.1181 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.45925 | 0.93157 | 0.48043 | 0.89223 | 0.68633 | 0.68633 | 0.60865 | 0.76603 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633 | 0.68633
Marulan 132 kV | 7.2336 | 7.2336 | 7.2336 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.0081 | 9.5284 | 6.4831 | 12.0401 | 9.2616 | 9.2616 | 8.3288 | 10.1959 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616 | 9.2616
Molong 66 kV | 0.6913 | 0.69164 | 0.69164 | 1.2265 | 1.2265 | 2.1674 | 1.2265 | 0.94053 | 1.5136 | 1.5171 | 1.5944 | 1.2265 | 2.1674 | 1.9493 | 1.3498 | 2.1674 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.1674 | 1.2265 | 2.1674
Moree 66 kV | 1.5674 | 1.5675 | 1.5675 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.5604 | 1.1102 | 0.57729 | 1.0721 | 0.8247 | 0.8247 | 0.73013 | 0.92197 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247 | 0.8247
Morven 132 kV | 1.3308 | 1.3308 | 1.3308 | 1.7704 | 1.7704 | 1.7704 | 1.0849 | 1.2392 | 1.4103 | 1.2392 | 1.4103 | 1.7704 | 1.7704 | 1.5934 | 1.9473 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704 | 1.7704
Mount Piper 66 kV | 3.3622 | 3.3637 | 3.3637 | 5.851 | 5.851 | 5.851 | 0.57173 | 4.4461 | 7.2713 | 4.0957 | 7.6063 | 5.851 | 5.851 | 5.2578 | 6.446 | 5.851 | 5.851 | 5.851 | 5.851 | 0.57173 | 5.851 | 0.57173 | 5.851
Mudgee 132 kV | 0.52864 | 0.52864 | 0.52864 | 2.2316 | 2.2316 | 2.2316 | 2.2316 | 1.5621 | 2.901 | 1.5621 | 2.901 | 2.2316 | 2.2316 | 2.0085 | 2.4546 | 2.2316 | 2.2316 | 2.2316 | 2.2316 | 0.36159 | 2.2316 | 0.36159 | 4.839
Munmorah 132 kV | 11.1424 | 11.1427 | 11.1427 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 3.0801 | 17.2023 | 10.1373 | 4.5933 | 3.5333 | 14.4819 | 13.0268 | 3.9088 | 14.4819 | 14.4819 | 14.4819 | 14.4819 | 3.5333 | 14.4819 | 3.5333 | 26.5934
Munmorah 330 kV (via old Power Stn Txs) | 4.903 | 4.9034 | 4.9034 | 9.9648 | 9.9648 | 9.9648 | 9.9648 | 7.0567 | 12.8904 | 6.9754 | 12.9542 | 9.9648 | 9.9648 | 8.9598 | 10.9718 | 9.9648 | 9.9648 | 9.9648 | 9.9648 | 1.4618 | 9.9648 | 1.4618 | 22.8869
Munyang 33 kV | 3.1221 | 3.1234 | 3.1234 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 0.74511 | 1.3662 | 0.73894 | 1.3723 | 1.0556 | 1.0556 | 0.9501 | 1.1612 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556 | 1.0556
Murrumbateman 132 kV | 0.9981 | 0.9981 | 0.9981 | 1.6136 | 1.6136 | 6.8747 | 1.6136 | 1.1295 | 2.0977 | 1.6776 | 2.0977 | 1.6136 | 1.6136 | 1.4523 | 1.7749 | 1.6136 | 1.6136 | 1.6136 | 1.6136 | 1.6136 | 6.8747 | 1.6136 | 6.8747
Murrumburrah 66 kV | 1.6076 | 1.6077 | 1.6077 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 3.8977 | 7.1127 | 3.8512 | 7.1522 | 5.5017 | 5.5017 | 4.9482 | 6.056 | 5.5017 | 5.5017 | 5.5017 | 5.5017 | 1.0847 | 5.5017 | 1.0847 | 5.5017
Muswellbrook 132 kV | 9.8864 | 9.8871 | 9.8871 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 3.1683 | 5.2791 | 2.8505 | 5.2938 | 4.0722 | 4.0722 | 3.6496 | 4.4982 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722 | 4.0722
Nambucca 66 kV | 1.7796 | 1.7799 | 1.7799 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 1.7671 | 3.2329 | 1.7495 | 3.2491 | 2.4993 | 2.4993 | 2.2487 | 2.75 | 2.4993 | 2.4993 | 2.4993 | 2.4993 | 1.6852 | 2.4993 | 1.6852 | 2.4993
Narrabri 66 kV | 0.91398 | 0.91415 | 0.91415 | 1.1622 | 1.1622 | 6.0966 | 0.95635 | 0.84345 | 1.1749 | 0.81351 | 1.2433 | 1.1622 | 1.1622 | 1.025 | 1.055 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 6.0966
Newcastle 132 kV | 0.99829 | 0.99869 | 0.99869 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.3921 | 3.0478 | 1.8983 | 3.5255 | 2.7119 | 2.7119 | 2.4313 | 2.9947 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119 | 2.7119
Orange North 132 kV | 7.208 | 2.7236 | 2.7236 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 5.4891 | 10.0096 | 5.4157 | 10.0578 | 7.7367 | 7.7367 | 6.9316 | 8.5489 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367
Orange 66 kV | 1.2765 | 1.2765 | 1.2765 | 1.0615 | 1.0615 | 1.0615 | 0.82782 | 0.81341 | 0.9622 | 0.74308 | 1.0762 | 0.82782 | 1.0615 | 0.93129 | 0.91436 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615
Panorama 66 kV | 2.974 | 2.9742 | 2.9742 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 1.5192 | 2.5315 | 1.5649 | 2.5387 | 1.9529 | 2.2356 | 1.9793 | 2.1572 | 2.2356 | 1.9529 | 1.9529 | 1.9529 | 1.9529 | 6.0093 | 1.9529 | 6.0093
Parkes 132 kV | 4.0585 | 0.66894 | 0.66894 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 2.1652 | 4.6908 | 2.3455 | 4.3559 | 3.3507 | 3.3507 | 2.9385 | 3.7801 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507 | 3.3507
Parkes 66 kV | 2.6642 | 2.6659 | 2.6659 | 8.2898 | 8.2898 | 8.2898 | 0.87157 | 6.0838 | 10.5107 | 5.8029 | 10.7768 | 8.2898 | 8.2898 | 7.4533 | 9.1281 | 8.2898 | 8.2898 | 8.2898 | 8.2898 | 1.5996 | 8.2898 | 1.5996 | 8.2898
Port Macquarie 33 kV | 2.2524 | 2.2528 | 2.2528 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 4.516 | 8.2914 | 4.4748 | 8.3102 | 6.3925 | 6.3925 | 5.742 | 7.0455 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 6.3925 | 0.60157 | 6.3925
Queanbeyan 66 kV | 3.9991 | 3.9995 | 3.9995 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 0.85001 | 1.5622 | 5.0273 | 1.5679 | 1.2061 | 7.1819 | 6.441 | 1.3267 | 7.1819 | 1.2061 | 1.2061 | 1.2061 | 1.2061 | 7.1819 | 1.2061 | 7.1819
Raleigh 132 kV | 1.9773 | 1.9776 | 1.9776 | 1.8918 | 1.8918 | 2.899 | 1.8918 | 2.0276 | 2.4624 | 2.0293 | 2.4594 | 1.8918 | 1.8918 | 1.702 | 2.0818 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918 | 1.8918
Regentville 132 kV | 11.3734 | 11.3742 | 11.3742 | 19.7476 | 19.7476 | 31.5849 | 19.7476 | 13.9977 | 25.531 | 22.1094 | 25.6719 | 19.7476 | 19.7476 | 17.7564 | 21.7425 | 19.7476 | 19.7476 | 19.7476 | 19.7476 | 1.4236 | 31.5849 | 1.4236 | 31.5849
Rookwood Road 132 kV | 5.3888 | 5.3892 | 5.3892 | 0.19399 | 10.0207 | 0.19399 | 0.19399 | 0.81115 | 0.23608 | 0.6113 | 0.25219 | 0.19399 | 0.19399 | 0.16924 | 0.21968 | 0.19399 | 0.19399 | 0.19399 | 8.5716 | 0.19399 | 8.5716 | 0.19399 | 8.5716
Snowy Adit 132 kV | 1.6166 | 1.6167 | 1.6167 | 2.6538 | 2.6538 | 2.6538 | 1.4641 | 1.8576 | 2.7065 | 1.8576 | 2.7065 | 2.6538 | 2.6538 | 2.3885 | 2.919 | 2.6538 | 2.6538 | 2.6538 | 2.6538 | 2.0771 | 2.6538 | 2.0771 | 3.8003
Stroud 132 kV | 1.2057 | 1.2057 | 1.2057 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 2.9842 | 5.5887 | 2.9968 | 5.5654 | 4.2811 | 4.2811 | 3.8477 | 4.7156 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811 | 4.2811
Sydney East 132 kV | 2.459 | 2.4591 | 2.4591 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 2.1726 | 4.2849 | 2.2362 | 4.1529 | 3.1945 | 3.1945 | 2.8407 | 3.556 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 3.1945 | 22.2734
Sydney North 132 kV | 1.085 | 1.0854 | 1.0854 | 0.85754 | 3.0856 | 0.85754 | 0.85754 | 0.767 | 0.98806 | 0.60028 | 1.1148 | 0.85754 | 0.85754 | 0.79203 | 0.99037 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754
Sydney South 132 kV | 1.1822 | 1.1828 | 1.1828 | 0.85021 | 2.8781 | 0.85021 | 0.85021 | 0.77567 | 0.97366 | 0.59515 | 1.1053 | 0.85021 | 0.85021 | 0.79538 | 0.98624 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021
Sydney West 132 kV | 7.5954 | 7.5967 | 7.5967 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 0.81424 | 7.9082 | 5.2901 | 1.4545 | 7.5573 | 7.5573 | 6.7724 | 8.3487 | 7.5573 | 7.5573 | 7.5573 | 7.5573 | 1.1189 | 7.5573 | 1.1189 | 7.5573
Tamworth 66 kV | 3.968 | 3.9683 | 3.9683 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 1.8863 | 3.1432 | 1.9432 | 3.152 | 2.4246 | 2.4246 | 2.4577 | 2.6783 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 2.4246 | 15.514 | 2.4246 | 15.514
Taree 33 kV | 2.5576 | 2.5593 | 2.5593 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 4.4154 | 7.4337 | 4.1428 | 7.6938 | 5.9183 | 5.9183 | 5.3199 | 6.5181 | 5.9183 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 5.9183 | 3.66 | 5.9183
Taree 66 kV | 3.9226 | 3.9243 | 3.9243 | 0.91564 | 0.91564 | 11.2735 | 0.91564 | 0.66544 | 0.92535 | 0.64095 | 1.1903 | 0.91564 | 0.91564 | 0.80757 | 1.0274 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 11.2735
Tenterfield 22 kV | 1.1864 | 1.1866 | 1.1866 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.0817 | 2.706 | 2.0631 | 1.6422 | 1.2632 | 2.9473 | 2.6519 | 1.39 | 2.9473 | 2.9473 | 2.9473 | 2.9473 | 1.2632 | 2.9473 | 1.2632 | 2.9473
Tomago 132 Note 3 | 32.4598 | 32.4604 | 32.4604 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 22.8124 | 42.4903 | 22.7489 | 42.2479 | 32.4984 | 32.4984 | 28.996 | 36.0571 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 32.4984 | 2.81 | 32.4984
Tomago 330 kV | 49.93 | 49.9721 | 49.9721 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 110.593 | 201.1949 | 108.6327 | 201.7464 | 155.1895 | 155.1895 | 138.0461 | 172.695 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895 | 155.1895
Tuggerah 132 kV | 8.0779 | 8.0785 | 8.0785 | 15.2431 | 15.2431 | 15.2431 | 2.2795 | 10.7952 | 19.7152 | 10.6702 | 19.8161 | 15.2431 | 15.2431 | 13.707 | 16.782 | 15.2431 | 15.2431 | 15.2431 | 15.2431 | 2.6107 | 15.2431 | 2.6107 | 34.3799
Tumut 66 kV | 1.5272 | 1.5273 | 1.5273 | 3.4583 | 3.4583 | 7.2129 | 1.3719 | 0.93225 | 4.4782 | 2.4208 | 1.7834 | 1.3719 | 3.4583 | 3.1098 | 1.5337 | 3.4583 | 3.4583 | 3.4583 | 3.4583 | 1.3719 | 3.4583 | 1.3719 | 7.2129
Vales Pt 132 kV | 4.2778 | 4.2806 | 4.2806 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 1.6369 | 1.0139 | 12.4223 | 1.1038 | 0.84904 | 17.7462 | 15.9523 | 0.94859 | 17.7462 | 0.84904 | 0.84904 | 0.84904 | 0.84904 | 17.7462 | 0.84904 | 17.7462
Vineyard 132 kV | 16.8556 | 16.8569 | 16.8569 | 1.683 | 1.683 | 60.1784 | 1.683 | 2.7664 | 2.441 | 42.1249 | 2.1879 | 1.683 | 60.1784 | 54.1271 | 1.9286 | 60.1784 | 1.683 | 1.683 | 1.683 | 1.683 | 60.1784 | 1.683 | 96.7024
Wagga 66 kV | 3.2763 | 3.2768 | 3.2768 | 12.3577 | 12.3577 | 12.3577 | 0.57925 | 8.8731 | 14.9577 | 8.6504 | 15.1529 | 12.3577 | 12.3577 | 11.1086 | 13.6099 | 12.3577 | 12.3577 | 12.3577 | 12.3577 | 1.7012 | 12.3577 | 1.7012 | 12.3577
Wagga North 132 kV | 2.27 | 3.0528 | 3.0528 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.1238 | 3.6079 | 1.9317 | 3.5875 | 2.7596 | 2.7596 | 2.4791 | 3.0412 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 2.7596
Wagga North 66 kV | 3.733 | 3.7348 | 3.7348 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 3.1673 | 5.015 | 2.8622 | 5.3155 | 4.0889 | 4.0889 | 3.6778 | 4.5004 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889 | 4.0889
Wallerawang 132 kV Note 3 | 4.551 | 4.5529 | 4.5529 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 8.5331 | 15.2405 | 8.3134 | 15.4392 | 11.8764 | 11.8764 | 10.6783 | 13.0769 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 11.8764 | 1.6726 | 11.8764
Wallerawang 66 kV | 1.2057 | 1.2057 | 1.2057 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.64612 | 1.0496 | 0.59281 | 1.1009 | 0.84687 | 0.84687 | 0.76112 | 0.93287 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687 | 0.84687
Waratah West 132 kV | 6.2694 | 6.2699 | 6.2699 | 2.5513 | 2.5513 | 2.5513 | 2.2276 | 1.7333 | 2.8879 | 1.7859 | 3.3166 | 2.5513 | 2.5513 | 2.2586 | 2.4607 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 2.5513 | 28.7586
Wellington 132 kV Note 3 | 3.2553 | 5.7025 | 5.7025 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 4.1296 | 7.572 | 4.0889 | 7.5936 | 5.8412 | 5.8412 | 5.2351 | 6.4523 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 5.8412 | 27.0563
Wellington Town | 0.96416 | 0.96416 | 0.96416 | 4.9655 | 4.9655 | 4.9655 | 1.5589 | 3.4759 | 6.4552 | 3.4759 | 6.4552 | 4.9655 | 4.9655 | 4.4691 | 5.4619 | 4.9655 | 4.9655 | 4.9655 | 4.9655 | 1.5589 | 4.9655 | 0.91791 | 4.9655
Williamsdale 132 kV Note 3 | 2.5851 | 2.5853 | 2.5853 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 5.4861 | 6.901 | 4.3275 | 8.0368 | 6.1822 | 6.1822 | 5.5509 | 6.8163 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822
Yanco 33 kV | 1.9124 | 1.9137 | 1.9137 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 1.5647 | 10.7944 | 6.2018 | 1.5725 | 1.2096 | 8.8597 | 7.9606 | 1.3405 | 8.8597 | 8.8597 | 8.8597 | 8.8597 | 1.2096 | 8.8597 | 1.2096 | 8.8597
Yass 132 kV | 1.5988 | 1.3403 | 1.3403 | 1.2984 | 1.2984 | 2.5608 | 0.24648 | 1.7845 | 0.33457 | 1.7925 | 0.32042 | 1.2984 | 1.2984 | 1.1653 | 1.4323 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 1.2984
Yass 66 kV | 2.1015 | 2.1018 | 2.1018 | 1.072 | 1.072 | 3.5196 | 1.072 | 0.847 | 1.3073 | 0.75043 | 1.3937 | 1.072 | 1.072 | 0.95963 | 1.1856 | 1.072 | 1.072 | 1.072 | 1.072 | 1.072 | 3.5196 | 1.072 | 1.072
|  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## summary_MWh_optconting
Optimal contingency EUE (MWh) | DR | out23_0 | _input0 | basecase | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130
Albury 132 kV | 4.1977 | 4.2 | 4.2 | 12.14 | 12.14 | 20.69 | 0.7 | 8.46 | 15.87 | 8.5 | 15.79 | 12.14 | 12.14 | 10.91 | 13.38 | 12.14 | 12.14 | 12.14 | 12.14 | 0.7 | 20.69 | 0.7 | 20.69 | x
ANM 132 kV | 24.997 | 25.01 | 25.01 | 6.59 | 6.59 | 8.54 | 6.59 | 5.52 | 8.67 | 5.98 | 8.57 | 6.59 | 6.59 | 7.49 | 7.28 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59
Armidale 66 kV | 1.592 | 1.59 | 1.59 | 1.26 | 1.26 | 1.26 | 1.26 | 1.05 | 1.22 | 0.88 | 1.64 | 1.26 | 1.26 | 1.12 | 1.41 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 5.36
Balranald 22 kV | 2.4698 | 2.47 | 2.47 | 11.35 | 11.35 | 11.35 | 2.8 | 8.01 | 14.69 | 7.95 | 14.76 | 11.35 | 11.35 | 10.22 | 12.49 | 11.35 | 11.35 | 11.35 | 11.35 | 2.8 | 11.35 | 2.8 | 11.35
Beaconsfield 132 kV | 6.5465 | 6.55 | 6.55 | 0.27 | 6.99 | 0.27 | 0.27 | 0.23 | 0.32 | 3.95 | 0.35 | 0.27 | 5.64 | 5.07 | 0.3 | 5.64 | 0.27 | 0.27 | 5.64 | 0.27 | 5.64 | 0.27 | 5.64
Beryl 66 kV | 2.6123 | 2.61 | 2.61 | 2.09 | 2.09 | 10.67 | 2.09 | 1.62 | 2.71 | 7.47 | 2.71 | 2.09 | 10.67 | 9.6 | 2.31 | 10.67 | 2.09 | 2.09 | 2.09 | 2.09 | 10.67 | 2.09 | 10.67
Boambee South 132 kV | 0.84396 | 0.84 | 0.84 | 3.43 | 3.43 | 3.43 | 3.43 | 2.39 | 4.46 | 2.4 | 4.45 | 3.43 | 3.43 | 3.08 | 3.77 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 0.75 | 3.43
Boggabri East | 2.632 | 2.63 | 2.63 | 7.55 | 7.55 | 23.29 | 7.55 | 5.35 | 9.76 | 16.3 | 9.82 | 7.55 | 23.29 | 20.96 | 8.31 | 7.55 | 7.55 | 7.55 | 7.55 | 7.55 | 23.29 | 7.55 | 23.29
Boggabri North | 4.9351 | 4.94 | 4.94 | 14.16 | 14.16 | 27.6 | 14.16 | 10.03 | 18.3 | 9.91 | 18.41 | 14.16 | 14.16 | 12.74 | 15.58 | 14.16 | 14.16 | 14.16 | 14.16 | 14.16 | 14.16 | 14.16 | 27.6
Brandy Hill 132 kV | 1.118 | 1.12 | 1.12 | 0.85 | 0.85 | 0.85 | 0.85 | 0.58 | 1.15 | 0.6 | 1.11 | 0.85 | 0.85 | 0.76 | 0.96 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
Broken Hill 22 kV | 1.5527 | 1.55 | 1.55 | 3.98 | 3.98 | 11.85 | 3.98 | 2.8 | 5.15 | 8.29 | 5.17 | 3.98 | 11.85 | 10.64 | 4.38 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 11.85 | 3.98 | 11.85
Broken Hill 220 kV | 49.266 | 0.93 | 0.93 | 1.19 | 1.19 | 1.19 | 1.19 | 0.83 | 1.55 | 0.83 | 1.55 | 1.19 | 1.19 | 1.07 | 1.31 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19
Canberra 132 kV Note 3 | 8.0808 | 8.08 | 8.08 | 4.94 | 4.94 | 4.94 | 4.94 | 3.77 | 6.16 | 3.46 | 6.42 | 4.94 | 4.94 | 4.42 | 5.46 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94
Casino 132 kV | 0.64878 | 0.65 | 0.65 | 1.41 | 1.41 | 3.44 | 1.41 | 0.99 | 1.83 | 2.41 | 1.83 | 1.41 | 1.41 | 3.09 | 1.55 | 1.41 | 1.41 | 1.41 | 1.41 | 1.41 | 3.44 | 1.41 | 3.44
Coffs Harbour 66 kV | 2.6914 | 2.69 | 2.69 | 1.45 | 1.45 | 2.47 | 0.6 | 1.81 | 0.75 | 1.73 | 0.79 | 1.45 | 1.45 | 1.29 | 1.62 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45
Coleambally 132 kV | 1.4534 | 1.45 | 1.45 | 2.13 | 2.13 | 3.35 | 2.13 | 1.49 | 2.77 | 2.35 | 2.77 | 2.13 | 3.35 | 3.02 | 2.34 | 3.35 | 2.13 | 2.13 | 2.13 | 2.13 | 3.35 | 2.13 | 3.35
Cooma 11 kV | 1.0618 | 1.06 | 1.06 | 2.56 | 2.56 | 3.7 | 0.28 | 2.61 | 2.08 | 2.59 | 2.09 | 2.56 | 2.56 | 2.3 | 2.82 | 2.56 | 2.56 | 2.56 | 2.56 | 1.31 | 2.56 | 1.31 | 2.56
Cooma 66 kV | 1.7152 | 1.72 | 1.72 | 1.87 | 1.87 | 1.87 | 1.87 | 1.33 | 2.42 | 1.31 | 2.43 | 1.87 | 1.87 | 1.68 | 2.06 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
Cooma 132 kV | 6.1492 | 1.64 | 1.64 | 3.75 | 3.75 | 3.75 | 3.75 | 2.61 | 4.88 | 2.62 | 4.87 | 3.75 | 3.75 | 3.37 | 4.12 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75
Cowra 66 kV | 3.197 | 3.2 | 3.2 | 4.17 | 4.17 | 4.17 | 4.17 | 3.12 | 5.22 | 2.92 | 5.42 | 4.17 | 4.17 | 3.74 | 4.59 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17
Dapto 132 kV | 9.1755 | 9.18 | 9.18 | 18.5 | 18.5 | 18.5 | 18.5 | 12.91 | 24.21 | 12.95 | 24.05 | 18.5 | 18.5 | 16.57 | 20.45 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5
Darlington Point 132 kV Note 3 | 1.9205 | 1.92 | 1.92 | 0.59 | 0.59 | 0.59 | 0.59 | 0.42 | 0.76 | 0.41 | 0.76 | 0.59 | 0.59 | 0.53 | 0.65 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59
Deniliquin 66 kV | 1.9291 | 1.93 | 1.93 | 6.98 | 6.98 | 6.98 | 1.42 | 4.95 | 9.03 | 4.89 | 1.84 | 1.42 | 6.98 | 6.28 | 1.59 | 6.98 | 6.98 | 6.98 | 6.98 | 1.42 | 6.98 | 1.42 | 6.98
Dorrigo 132 kV | 0.85493 | 0.86 | 0.86 | 0.83 | 0.83 | 4.23 | 0.72 | 0.51 | 1.08 | 2.96 | 1.08 | 0.83 | 0.83 | 0.75 | 0.92 | 0.83 | 0.83 | 0.83 | 0.83 | 0.72 | 4.23 | 0.72 | 0.83
Finley 132 kV | 2.4597 | 0.66 | 0.66 | 3 | 3 | 3 | 3 | 2.09 | 3.91 | 2.1 | 3.9 | 3 | 3 | 2.7 | 3.3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.61 | 3
Finley 66 kV | 0.80378 | 0.8 | 0.8 | 1.59 | 1.59 | 5.1 | 0.38 | 2.21 | 2.05 | 3.57 | 2.06 | 1.59 | 1.59 | 3.3 | 1.75 | 1.59 | 1.59 | 1.59 | 1.59 | 0.38 | 3.67 | 0.38 | 3.67
Forbes 66 kV | 1.3262 | 1.33 | 1.33 | 4.77 | 4.77 | 4.77 | 0.94 | 3.38 | 6.17 | 3.34 | 6.2 | 4.77 | 4.77 | 4.29 | 5.25 | 4.77 | 4.77 | 4.77 | 4.77 | 0.94 | 4.77 | 0.94 | 4.77
Gadara (132 kV & 11 kV) | 17.479 | 17.48 | 17.48 | 6.79 | 6.79 | 11.49 | 6.79 | 4.8 | 8.8 | 4.76 | 8.83 | 6.79 | 6.79 | 6.11 | 7.48 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 90.21
Glen Innes 66 kV | 1.2788 | 1.28 | 1.28 | 2.09 | 2.09 | 3.5 | 2.09 | 1.51 | 2.68 | 2.45 | 2.72 | 2.09 | 3.5 | 3.15 | 2.3 | 3.5 | 2.09 | 2.09 | 2.09 | 1.31 | 3.5 | 2.09 | 3.5
Griffith 33 kV | 2.9845 | 2.98 | 2.98 | 6.72 | 6.72 | 6.72 | 6.72 | 4.72 | 8.72 | 4.7 | 8.73 | 6.72 | 6.72 | 6.04 | 7.39 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 1.27 | 15.16
Gunnedah 66 kV | 1.0449 | 1.04 | 1.04 | 3.87 | 3.87 | 3.87 | 0.69 | 2.74 | 5.01 | 2.71 | 5.04 | 3.87 | 3.87 | 3.48 | 4.26 | 3.87 | 3.87 | 3.87 | 3.87 | 0.69 | 3.87 | 0.69 | 3.87
Hawks Nest 132 kV | 1.3308 | 1.33 | 1.33 | 2.15 | 2.15 | 2.15 | 2.15 | 1.51 | 2.8 | 1.51 | 2.8 | 2.15 | 2.15 | 1.94 | 2.37 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 1.84
Haymarket 132 kV | 8.041 | 8.04 | 8.04 | 0.22 | 9.18 | 0.22 | 0.22 | 0.17 | 0.26 | 4.78 | 0.28 | 0.22 | 0.22 | 0.19 | 0.24 | 0.22 | 0.22 | 0.22 | 6.83 | 0.22 | 6.83 | 0.22 | 23.43
Herons Creek | 1.6166 | 1.62 | 1.62 | 1.24 | 1.24 | 2.95 | 0.45 | 2.07 | 0.58 | 2.07 | 0.58 | 1.24 | 2.06 | 1.85 | 1.37 | 2.06 | 1.24 | 1.24 | 1.24 | 1.24 | 2.06 | 1.24 | 2.06
Holroyd 132 kV | 17.9376 | 17.94 | 17.94 | 57.28 | 57.28 | 57.28 | 57.28 | 41.51 | 73.17 | 40.1 | 74.46 | 57.28 | 57.28 | 51.45 | 63.04 | 57.28 | 57.28 | 2.08 | 57.28 | 48.29 | 57.28 | 2.08 | 57.28
Ilford 132 kV | 1.4249 | 1.43 | 1.43 | 0.83 | 0.83 | 2.11 | 0.83 | 1.16 | 1.07 | 1.16 | 1.07 | 0.83 | 2.11 | 1.9 | 0.91 | 1.65 | 0.83 | 0.83 | 0.83 | 0.83 | 2.11 | 0.83 | 2.11
Ingleburn 66 kV | 1.8801 | 1.88 | 1.88 | 4.55 | 4.55 | 4.55 | 0.6 | 0.6 | 5.71 | 3.18 | 0.78 | 4.55 | 4.55 | 4.09 | 5 | 4.55 | 4.55 | 4.55 | 4.55 | 0.6 | 4.55 | 0.6 | 4.55
Inverell 66 kV | 2.8819 | 2.88 | 2.88 | 8.66 | 8.66 | 8.66 | 5.31 | 4.54 | 10.81 | 6.06 | 8.08 | 5.31 | 8.66 | 7.78 | 6.85 | 8.66 | 6.22 | 8.66 | 8.66 | 5.31 | 8.66 | 5.31 | 8.66
Kempsey 33 kV | 2.2038 | 2.2 | 2.2 | 1.56 | 1.56 | 8.07 | 1.56 | 1.24 | 1.9 | 1.09 | 2.03 | 1.56 | 1.56 | 1.39 | 1.72 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 8.07 | 1.56 | 8.07
Koolkhan 66 kV | 2.6198 | 2.62 | 2.62 | 6.33 | 6.33 | 7.46 | 5.38 | 5.27 | 6.98 | 5.22 | 7 | 6.33 | 6.33 | 5.69 | 6.97 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 0.34 | 6.33
Liddell 330 kV (33 kV supply via Mac Gen) | 2.0474 | 2.05 | 2.05 | 0.29 | 0.29 | 1.82 | 0.29 | 1.22 | 0.38 | 1.28 | 0.37 | 0.29 | 0.49 | 0.42 | 0.32 | 0.49 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
Lismore 132 kV Note 3 | 4.264 | 4.27 | 4.27 | 2.47 | 2.47 | 17.23 | 2.47 | 1.92 | 3.2 | 1.98 | 3.21 | 2.47 | 2.83 | 2.5 | 2.73 | 2.83 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 17.23
Liverpool 132 kV | 2.8851 | 2.89 | 2.89 | 7.62 | 7.62 | 20.61 | 0.86 | 5.36 | 7.26 | 5.33 | 7.28 | 5.6 | 7.62 | 6.85 | 6.16 | 7.62 | 5.6 | 7.62 | 7.62 | 0.86 | 7.62 | 0.86 | 18.86
Macarthur 132 kV | 1.9759 | 2.24 | 2.24 | 0.96 | 0.96 | 0.96 | 0.96 | 0.69 | 1.24 | 0.67 | 1.25 | 0.96 | 0.96 | 0.85 | 1.07 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.76 | 0.96
Macarthur 66 kV | 0.43366 | 0.43 | 0.43 | 0.59 | 0.59 | 0.59 | 0.59 | 0.42 | 0.76 | 0.41 | 0.77 | 0.59 | 0.59 | 0.53 | 0.65 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 5.89
Macksville 132 kV | 1.7796 | 1.78 | 1.78 | 1.69 | 1.69 | 2.88 | 0.8 | 2.01 | 2.2 | 2.01 | 2.2 | 1.69 | 1.69 | 2.59 | 1.86 | 1.69 | 1.69 | 1.69 | 1.69 | 0.8 | 1.69 | 0.8 | 1.69
Manildra 132 kV | 1.118 | 1.12 | 1.12 | 0.69 | 0.69 | 0.69 | 0.69 | 0.46 | 0.93 | 0.48 | 0.89 | 0.69 | 0.69 | 0.61 | 0.77 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69
Marulan 132 kV | 7.2336 | 7.23 | 7.23 | 9.26 | 9.26 | 9.26 | 9.26 | 9.01 | 9.53 | 6.48 | 12.04 | 9.26 | 9.26 | 8.33 | 10.2 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26
Molong 66 kV | 0.6913 | 0.69 | 0.69 | 1.23 | 1.23 | 2.17 | 1.23 | 0.94 | 1.51 | 1.52 | 1.59 | 1.23 | 2.17 | 1.95 | 1.35 | 2.17 | 1.23 | 1.23 | 1.23 | 1.23 | 2.17 | 1.23 | 2.17
Moree 66 kV | 1.5674 | 1.57 | 1.57 | 0.82 | 0.82 | 0.82 | 0.82 | 0.56 | 1.11 | 0.58 | 1.07 | 0.82 | 0.82 | 0.73 | 0.92 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
Morven 132 kV | 1.3308 | 1.33 | 1.33 | 1.77 | 1.77 | 1.77 | 1.08 | 1.24 | 1.41 | 1.24 | 1.41 | 1.77 | 1.77 | 1.59 | 1.95 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77
Mount Piper 66 kV | 3.3622 | 3.36 | 3.36 | 5.85 | 5.85 | 5.85 | 0.57 | 4.45 | 7.27 | 4.1 | 7.61 | 5.85 | 5.85 | 5.26 | 6.45 | 5.85 | 5.85 | 5.85 | 5.85 | 0.57 | 5.85 | 0.57 | 5.85
Mudgee 132 kV | 0.52864 | 0.53 | 0.53 | 2.23 | 2.23 | 2.23 | 2.23 | 1.56 | 2.9 | 1.56 | 2.9 | 2.23 | 2.23 | 2.01 | 2.45 | 2.23 | 2.23 | 2.23 | 2.23 | 0.36 | 2.23 | 0.36 | 4.84
Munmorah 132 kV | 11.1424 | 2.46 | 2.46 | 14.48 | 14.48 | 14.48 | 1.41 | 0.96 | 17.2 | 10.14 | 1.84 | 3.53 | 14.48 | 13.03 | 1.58 | 14.48 | 1.41 | 14.48 | 14.48 | 1.41 | 14.48 | 1.41 | 26.59
Munmorah 330 kV (via old Power Stn Txs) | 4.903 | 4.9 | 4.9 | 9.96 | 9.96 | 9.96 | 9.96 | 7.06 | 12.89 | 6.98 | 12.95 | 9.96 | 9.96 | 8.96 | 10.97 | 9.96 | 9.96 | 9.96 | 9.96 | 1.46 | 9.96 | 1.46 | 22.89
Munyang 33 kV | 3.1221 | 3.12 | 3.12 | 1.27 | 1.27 | 1.27 | 1.27 | 0.9 | 1.65 | 0.89 | 1.65 | 1.27 | 1.27 | 1.15 | 1.4 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27 | 1.27
Murrumbateman 132 kV | 0.9981 | 1 | 1 | 1.61 | 1.61 | 6.87 | 1.61 | 1.13 | 2.1 | 4.81 | 2.1 | 1.61 | 6.87 | 6.19 | 1.77 | 6.87 | 1.61 | 1.61 | 1.61 | 1.61 | 6.87 | 1.61 | 6.87
Murrumburrah 66 kV | 1.6076 | 1.61 | 1.61 | 5.5 | 5.5 | 5.5 | 1.08 | 3.9 | 7.11 | 3.85 | 7.15 | 5.5 | 5.5 | 4.95 | 6.06 | 5.5 | 5.5 | 5.5 | 5.5 | 1.08 | 5.5 | 1.08 | 5.5
Muswellbrook 132 kV | 9.8864 | 9.89 | 9.89 | 4.07 | 4.07 | 4.07 | 4.07 | 3.17 | 5.28 | 2.85 | 5.29 | 4.07 | 4.07 | 3.65 | 4.5 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07
Nambucca 66 kV | 1.7796 | 1.78 | 1.78 | 2.5 | 2.5 | 2.5 | 1.69 | 1.77 | 3.23 | 1.75 | 3.25 | 2.5 | 2.5 | 2.25 | 2.75 | 2.5 | 2.5 | 2.5 | 2.5 | 1.69 | 2.5 | 1.69 | 2.5
Narrabri 66 kV | 0.91398 | 0.91 | 0.91 | 1.16 | 1.16 | 6.1 | 0.96 | 0.84 | 1.17 | 0.81 | 1.24 | 1.16 | 1.16 | 1.02 | 1.06 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 6.1
Newcastle 132 kV | 0.99829 | 1 | 1 | 2.71 | 2.71 | 2.71 | 2.71 | 2.39 | 3.05 | 1.9 | 3.53 | 2.71 | 2.71 | 2.43 | 2.99 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Orange North 132 kV | 7.208 | 2.72 | 2.72 | 7.74 | 7.74 | 7.74 | 7.74 | 5.49 | 10.01 | 5.42 | 10.06 | 7.74 | 7.74 | 6.93 | 8.55 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74
Orange 66 kV | 1.2765 | 1.28 | 1.28 | 1.06 | 1.06 | 1.06 | 0.83 | 0.81 | 0.96 | 0.74 | 1.08 | 0.83 | 1.06 | 0.93 | 0.91 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06
Panorama 66 kV | 2.974 | 2.97 | 2.97 | 1.95 | 1.95 | 6.01 | 1.95 | 1.52 | 2.53 | 1.56 | 2.54 | 1.95 | 2.24 | 1.98 | 2.16 | 2.24 | 1.95 | 1.95 | 1.95 | 1.95 | 6.01 | 1.95 | 6.01
Parkes 132 kV | 4.0585 | 0.67 | 0.67 | 3.35 | 3.35 | 3.35 | 3.35 | 2.17 | 4.69 | 2.35 | 4.36 | 3.35 | 3.35 | 2.94 | 3.78 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35
Parkes 66 kV | 2.6642 | 2.67 | 2.67 | 8.29 | 8.29 | 8.29 | 0.87 | 6.08 | 10.51 | 5.8 | 10.78 | 8.29 | 8.29 | 7.45 | 9.13 | 8.29 | 8.29 | 8.29 | 8.29 | 1.6 | 8.29 | 1.6 | 8.29
Port Macquarie 33 kV | 2.2524 | 2.25 | 2.25 | 6.39 | 6.39 | 6.39 | 6.39 | 4.52 | 8.29 | 4.47 | 8.31 | 6.39 | 6.39 | 5.74 | 7.05 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 0.6 | 6.39
Queanbeyan 66 kV | 3.9991 | 4 | 4 | 1.21 | 1.21 | 7.18 | 1.21 | 0.85 | 1.56 | 5.03 | 1.57 | 1.21 | 7.18 | 6.44 | 1.33 | 7.18 | 1.21 | 1.21 | 1.21 | 1.21 | 7.18 | 1.21 | 7.18
Raleigh 132 kV | 1.9773 | 1.98 | 1.98 | 1.89 | 1.89 | 2.9 | 1.89 | 2.03 | 2.46 | 2.03 | 2.46 | 1.89 | 1.89 | 1.7 | 2.08 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89
Regentville 132 kV | 11.3734 | 11.37 | 11.37 | 19.75 | 19.75 | 31.58 | 19.75 | 14 | 25.53 | 22.11 | 25.67 | 19.75 | 19.75 | 17.76 | 21.74 | 19.75 | 19.75 | 19.75 | 19.75 | 1.42 | 31.58 | 1.42 | 31.58
Rookwood Road 132 kV | 5.3888 | 5.39 | 5.39 | 0.19 | 10.02 | 0.19 | 0.19 | 0.81 | 0.24 | 0.61 | 0.25 | 0.19 | 0.19 | 0.17 | 0.22 | 0.19 | 0.19 | 0.19 | 8.57 | 0.19 | 8.57 | 0.19 | 8.57
Snowy Adit 132 kV | 1.6166 | 1.62 | 1.62 | 2.65 | 2.65 | 2.65 | 1.46 | 1.86 | 2.71 | 1.86 | 2.71 | 2.65 | 2.65 | 2.39 | 2.92 | 2.65 | 2.65 | 2.65 | 2.65 | 2.08 | 2.65 | 2.08 | 3.8
Stroud 132 kV | 1.2057 | 1.21 | 1.21 | 4.28 | 4.28 | 4.28 | 4.28 | 2.98 | 5.59 | 3 | 5.57 | 4.28 | 4.28 | 3.85 | 4.72 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28
Sydney East 132 kV | 2.459 | 2.46 | 2.46 | 3.19 | 3.19 | 3.19 | 3.19 | 2.17 | 4.28 | 2.24 | 4.15 | 3.19 | 3.19 | 2.84 | 3.56 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 22.27
Sydney North 132 kV | 1.085 | 1.09 | 1.09 | 0.86 | 3.09 | 0.86 | 0.86 | 0.77 | 0.99 | 0.6 | 1.11 | 0.86 | 0.86 | 0.79 | 0.99 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
Sydney South 132 kV | 1.1822 | 1.18 | 1.18 | 0.85 | 2.88 | 0.85 | 0.85 | 0.78 | 0.97 | 0.6 | 1.11 | 0.85 | 0.85 | 0.8 | 0.99 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
Sydney West 132 kV | 7.5954 | 7.6 | 7.6 | 7.56 | 7.56 | 7.56 | 1.12 | 0.81 | 7.91 | 5.29 | 1.45 | 7.56 | 7.56 | 6.77 | 8.35 | 7.56 | 7.56 | 7.56 | 7.56 | 1.12 | 7.56 | 1.12 | 7.56
Tamworth 66 kV | 3.968 | 3.97 | 3.97 | 2.42 | 2.42 | 15.51 | 2.42 | 1.89 | 3.14 | 1.94 | 3.15 | 2.42 | 2.42 | 2.46 | 2.68 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 15.51 | 2.42 | 15.51
Taree 33 kV | 2.5576 | 2.56 | 2.56 | 5.92 | 5.92 | 5.92 | 3.66 | 4.42 | 7.43 | 4.14 | 7.69 | 5.92 | 5.92 | 5.32 | 6.52 | 5.92 | 5.92 | 5.92 | 5.92 | 3.66 | 5.92 | 3.66 | 5.92
Taree 66 kV | 3.9226 | 3.92 | 3.92 | 0.92 | 0.92 | 11.27 | 0.92 | 0.67 | 0.93 | 0.64 | 1.19 | 0.92 | 0.92 | 0.81 | 1.03 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 11.27
Tenterfield 22 kV | 1.1864 | 1.19 | 1.19 | 2.95 | 2.95 | 2.95 | 1.26 | 2.08 | 2.71 | 2.06 | 1.64 | 1.26 | 2.95 | 2.65 | 1.39 | 2.95 | 2.95 | 2.95 | 2.95 | 1.26 | 2.95 | 1.26 | 2.95
Tomago 132 Note 3 | 32.4598 | 32.46 | 32.46 | 32.5 | 32.5 | 32.5 | 32.5 | 22.81 | 42.49 | 22.75 | 42.25 | 32.5 | 32.5 | 29 | 36.06 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 2.81 | 32.5
Tomago 330 kV | 49.93 | 49.97 | 49.97 | 155.19 | 155.19 | 155.19 | 155.19 | 110.59 | 201.19 | 108.63 | 201.75 | 155.19 | 155.19 | 138.05 | 172.69 | 155.19 | 155.19 | 155.19 | 155.19 | 155.19 | 155.19 | 155.19 | 155.19
Tuggerah 132 kV | 8.0779 | 8.08 | 8.08 | 15.24 | 15.24 | 15.24 | 2.28 | 10.8 | 19.72 | 10.67 | 19.82 | 15.24 | 15.24 | 13.71 | 16.78 | 15.24 | 15.24 | 15.24 | 15.24 | 2.61 | 15.24 | 2.61 | 34.38
Tumut 66 kV | 1.5272 | 1.53 | 1.53 | 3.46 | 3.46 | 7.21 | 1.37 | 0.93 | 4.48 | 2.42 | 1.78 | 1.37 | 3.46 | 3.11 | 1.53 | 3.46 | 3.46 | 3.46 | 3.46 | 1.37 | 3.46 | 1.37 | 7.21
Vales Pt 132 kV | 4.2778 | 4.28 | 4.28 | 0.85 | 0.85 | 17.75 | 0.85 | 1.64 | 1.01 | 12.42 | 1.1 | 0.85 | 17.75 | 15.95 | 0.95 | 17.75 | 0.85 | 0.85 | 0.85 | 0.85 | 17.75 | 0.85 | 17.75
Vineyard 132 kV | 16.8556 | 16.86 | 16.86 | 1.68 | 1.68 | 60.18 | 1.68 | 2.77 | 2.44 | 42.12 | 2.19 | 1.68 | 60.18 | 54.13 | 1.93 | 60.18 | 1.68 | 1.68 | 1.68 | 1.68 | 60.18 | 1.68 | 96.7
Wagga 66 kV | 3.2763 | 3.28 | 3.28 | 12.36 | 12.36 | 12.36 | 0.58 | 8.87 | 14.96 | 8.65 | 15.15 | 12.36 | 12.36 | 11.11 | 13.61 | 12.36 | 12.36 | 12.36 | 12.36 | 1.7 | 12.36 | 1.7 | 12.36
Wagga North 132 kV | 2.27 | 3.05 | 3.05 | 2.76 | 2.76 | 2.76 | 2.76 | 2.12 | 3.61 | 1.93 | 3.59 | 2.76 | 2.76 | 2.48 | 3.04 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76
Wagga North 66 kV | 3.733 | 3.73 | 3.73 | 4.09 | 4.09 | 4.09 | 4.09 | 3.17 | 5.02 | 2.86 | 5.32 | 4.09 | 4.09 | 3.68 | 4.5 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09
Wallerawang 132 kV Note 3 | 4.551 | 4.55 | 4.55 | 11.88 | 11.88 | 11.88 | 11.88 | 8.53 | 15.24 | 8.31 | 15.44 | 11.88 | 11.88 | 10.68 | 13.08 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 1.67 | 11.88
Wallerawang 66 kV | 1.2057 | 1.21 | 1.21 | 0.85 | 0.85 | 0.85 | 0.85 | 0.65 | 1.05 | 0.59 | 1.1 | 0.85 | 0.85 | 0.76 | 0.93 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
Waratah West 132 kV | 6.2694 | 6.27 | 6.27 | 2.55 | 2.55 | 2.55 | 2.23 | 1.73 | 2.89 | 1.79 | 3.32 | 2.55 | 2.55 | 2.26 | 2.46 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 28.76
Wellington 132 kV Note 3 | 3.2553 | 5.7 | 5.7 | 5.84 | 5.84 | 5.84 | 5.84 | 4.13 | 7.57 | 4.09 | 7.59 | 5.84 | 5.84 | 5.24 | 6.45 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 27.06
Wellington Town | 0.96416 | 0.96 | 0.96 | 4.99 | 4.99 | 4.99 | 4.99 | 3.49 | 6.49 | 3.49 | 6.49 | 4.99 | 4.99 | 4.49 | 5.49 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 0.92 | 4.99
Williamsdale 132 kV Note 3 | 2.5851 | 2.59 | 2.59 | 6.18 | 6.18 | 6.18 | 6.18 | 5.49 | 6.9 | 4.33 | 8.04 | 6.18 | 6.18 | 5.55 | 6.82 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18
Yanco 33 kV | 1.9124 | 1.91 | 1.91 | 8.86 | 8.86 | 8.86 | 1.21 | 1.56 | 10.79 | 6.2 | 1.57 | 1.21 | 8.86 | 7.96 | 1.34 | 8.86 | 8.86 | 8.86 | 8.86 | 1.21 | 8.86 | 1.21 | 8.86
Yass 132 kV | 1.5988 | 1.34 | 1.34 | 1.3 | 1.3 | 2.56 | 0.25 | 1.78 | 0.33 | 1.79 | 0.32 | 1.3 | 1.3 | 1.17 | 1.43 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Yass 66 kV | 2.1015 | 2.1 | 2.1 | 1.07 | 1.07 | 3.52 | 1.07 | 0.85 | 1.31 | 0.75 | 1.39 | 1.07 | 1.07 | 0.96 | 1.19 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 3.52 | 1.07 | 1.07
|  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## compliance_test
From TransGrid's compliance test dated 28 July 2016 |  |  |  | C optimisation results
|  |  | DR |  | MWh |  |  |  | minutes EUE @ avg demand |  |  |  | Would TG comply? |  |  |  | mins | line length km |  | ln 1 TTR |  | ln 2 TTR |  | Tx 1 TTR |  | Tx 2 TTR
| Expected unserved energy /year (MWh/year) | Unserved average minutes | IPART minutes | N-1 EUE | DR | out23_0 | _input0 | basecase | DR | out23_0 | _input0 | basecase | MWh | out23_0 | _input0 | minutes | compliance model/ C program | compliance model | C program | compliance model | C program | compliance model | C program | compliance model | C program | compliance model | C program
Albury 132 kV | 0.006577 | 0.0084479 | 4 | Albury 132 kV | 4.1977 | 4.1984 | 4.1984 | 12.1426 | 4.015 | 4.0157 | 4.0157 | 13.335 | 1 |  |  | 1 | 0.00063351 | 16.96 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
ANM 132 kV (Note r.) | 0 | 0 | 27 | ANM 132 kV | 24.997 | 25.0066 | 25.0066 | 6.593 | 26.7347 | 26.745 | 26.745 | 5.4189 | 1 |  |  | 1 | 0 | 106.21 | #REF! | 0 |  | 0 |  | 0 |  | 0
Armidale 66 kV | 0.047471 | 0.12144 | 5 | Armidale 66 kV | 1.592 | 1.592 | 1.592 | 1.5799 | 4.9289 | 4.9289 | 4.9289 | 6.446 | 1 |  |  | 1 | 0.018839 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Balranald 22 kV (refer comments) | 2.9819 | 111.0163 | 73 | Balranald 22 kV | 2.4698 | 2.4703 | 2.4703 | 3.0802 | 72.6404 | 72.6556 | 72.6556 | 114.0826 | 1 |  |  | 1 | 0.97312 | 397.8 | #REF! | 1 |  | 1 |  | 1 |  | 1
Beaconsfield West 132 kV (Note s.) | 0 | 0 | 0 | Beaconsfield 132 kV | 6.5465 | 6.547 | 6.547 | 5.3739 | 2.4765 | 2.4767 | 2.4767 | 1.6213 | 1 |  |  | 1 | 0 | 19.7 | #REF! | 0 |  | 0 |  | 0 |  | 0
Beryl 66 kV | 0.31246 | 0.61868 | 5 | Beryl 66 kV | 2.6123 | 2.6124 | 2.6124 | 2.8567 | 4.7281 | 4.7284 | 4.7284 | 4.6376 | 1 |  |  | 1 | 0.1334 | 124.5 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Boambee South 132 kV | 0.0044516 | 0.033032 | 5 | Boambee South 132 kV | 0.84396 | 0.84402 | 0.84402 | 3.4257 | 4.7281 | 4.7284 | 4.7284 | 17.1457 | 1 |  |  | 1 | 0.0019266 | 36.3 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Boggabri East 132 kV (Note q.) | #DIV/0! | #DIV/0! | 39 | Boggabri East | 2.632 | 2.6323 | 2.6323 | 8.641 | 38.7065 | 38.7103 | 38.7103 | 115.7279 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Boggabri North 132 kV (Note p.) | #DIV/0! | #DIV/0! | 39 | Boggabri North | 4.9351 | 4.9356 | 4.9356 | 16.2019 | 38.7065 | 38.7104 | 38.7104 | 115.7279 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Brandy Hill 132 kV (Note o.) | #VALUE! | #VALUE! | 13 | Brandy Hill 132 kV | 1.118 | 1.1181 | 1.1181 | 1.1281 | 13.1528 | 13.1547 | 13.1547 | 6.9778 | #VALUE! |  |  | #VALUE! | #VALUE! | 48.4 | #REF! | 0 |  | 0 |  | 0 |  | 0
Broken Hill 22 kV | 12.9754 | 42.3017 | 5 | Broken Hill 22 kV | 1.5527 | 1.5527 | 1.5527 | 4.2083 | 4.8071 | 4.8071 | 4.8071 | 13.8431 | 0 |  |  | 0 | 3.0558 | 259.5 | #REF! | 0.5 |  | 0 |  | 0 |  | 0.5
Broken Hill 220 kV (Note n.) | 25.8035 | 97.6637 | 252 | Broken Hill 220 kV | 49.266 | 0.93246 | 0.93246 | 1.1914 | 252 | 4.7696 | 4.7696 | 4.3323 | 0 |  |  | 0 | 22.543 | 259.5 | #REF! | 1 |  | 0 |  | 0 |  | 0
Canberra 132 kV | 0.682 | 0.12541 | 2 | Canberra 132 kV Note 3 | 8.0808 | 8.0811 | 8.0811 | 7.8274 | 1.9889 | 1.989 | 1.989 | 1.963 | 1 |  |  | 1 | 0.063888 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 84.2
Casino (tee) 132 kV | 0.085547 | 0.34864 | 3 | Casino 132 kV | 0.64878 | 0.64878 | 0.64878 | 1.4112 | 2.8269 | 2.8269 | 2.8269 | 6.272 | 1 |  |  | 1 | 0.055588 | 124 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Coffs Harbour 66 kV (Note s.) | 0.05585 | 0.089306 | 6 | Coffs Harbour 66 kV | 2.6914 | 2.6914 | 2.6914 | 4.0028 | 5.8636 | 5.8636 | 5.8636 | 9.3239 | 1 |  |  | 1 | 0.0095781 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Coleambally 132 kV | 0.0042663 | 0.056424 | 13 | Coleambally 132 kV | 1.4534 | 1.4536 | 1.4536 | 2.1305 | 13.1528 | 13.1548 | 13.1548 | 31.4392 | 1 |  |  | 1 | 0.0017947 | 152.7 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Cooma 11 kV (Note t.) | #DIV/0! | #DIV/0! | 10 | Cooma 11 kV | 1.0618 | 1.0627 | 1.0627 | 3.2576 | 9.609 | 9.617 | 9.617 | 27.8429 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Cooma 66 kV | 0.014518 | 0.16867 | 10 | Cooma 66 kV | 1.7152 | 1.7166 | 1.7166 | 1.8693 | 9.609 | 9.617 | 9.617 | 27.0129 | 1 |  |  | 1 | 0.0062439 | 79.4 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Cooma 132 kV | 0 | 0 | 15 | Cooma 132 kV | 6.1492 | 1.6386 | 1.6386 | 3.7453 | 14.4688 | 3.8556 | 3.8556 | 10.8037 | 1 |  |  | 1 | 0 | 79.4 | #REF! | 0 |  | 0 |  | 0 |  | 0
Cowra 66 kV | 0.020906 | 0.08382 | 13 | Cowra 66 kV | 3.197 | 3.1991 | 3.1991 | 5.3991 | 12.5373 | 12.5454 | 12.5454 | 24.9456 | 1 |  |  | 1 | 0.0033601 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Dapto 132 kV | 0 | 0 | 2 | Dapto 132 kV | 9.1755 | 9.1777 | 9.1777 | 24.4073 | 1.5945 | 1.5949 | 1.5949 | 3.9457 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Darlington Point 132 kV | 0 | 0 | 13 | Darlington Point 132 kV Note 3 | 1.9205 | 1.9221 | 1.9221 | 1.0323 | 12.5525 | 12.563 | 12.563 | 3.9104 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Deniliquin 66 kV | 0.16064 | 0.41589 | 5 | Deniliquin 66 kV | 1.9291 | 1.9292 | 1.9292 | 7.4369 | 4.7281 | 4.7284 | 4.7284 | 18.6678 | 1 |  |  | 1 | 0.022278 | 152.7 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Dorrigo (tee) 132 kV | 0.013874 | 0.41115 | 34 | Dorrigo 132 kV | 0.85493 | 0.85522 | 0.85522 | 0.83304 | 33.5268 | 33.538 | 33.538 | 40.3084 | 1 |  |  | 1 | 0.0102 | 139.8 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Finley 132 kV (Note m.) | #DIV/0! | #DIV/0! | 15 | Finley 132 kV | 2.4597 | 0.65546 | 0.65546 | 2.9986 | 14.4688 | 3.8556 | 3.8556 | 16.973 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 167.3 | #REF! | 0 |  | 0 |  | 0 |  | 0
Finley 66 kV | 0.071248 | 0.45494 | 5 | Finley 66 kV | 0.80378 | 0.80383 | 0.80383 | 1.7094 | 4.7281 | 4.7284 | 4.7284 | 11.8254 | 1 |  |  | 1 | 0.038472 | 167.3 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Forbes 66 kV | 0.060754 | 0.2229 | 5 | Forbes 66 kV | 1.3262 | 1.3263 | 1.3263 | 5.0746 | 4.7281 | 4.7284 | 4.7284 | 18.3068 | 1 |  |  | 1 | 0.012176 | 88.2 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Gadara (132 kV and 11 kV) (Note u.) | 0.1005 | 0.14709 | 29 | Gadara (132 kV & 11 kV) | 17.479 | 17.4801 | 17.4801 | 7.7423 | 29.3764 | 29.3783 | 29.3783 | 12.6923 | 1 |  |  | 1 | 0.011589 | 79.6 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Glen Innes 66 kV | 0.013288 | 0.097579 | 13 | Glen Innes 66 kV | 1.2788 | 1.2796 | 1.2796 | 3.0279 | 12.5373 | 12.5454 | 12.5454 | 42.0547 | 1 |  |  | 1 | 0.0023203 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Griffith 33 kV | 0.059314 | 0.089638 | 4 | Griffith 33 kV | 2.9845 | 2.9847 | 2.9847 | 6.9284 | 3.99 | 3.9903 | 3.9903 | 11.056 | 1 |  |  | 1 | 0.0081076 | 59.7 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Gunnedah 66 kV | 0.072925 | 0.32384 | 5 | Gunnedah 66 kV | 1.0449 | 1.045 | 1.045 | 4.0972 | 4.7281 | 4.7284 | 4.7284 | 18.8348 | 1 |  |  | 1 | 0.017193 | 66.4 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Hawks Nest (tee) 132 kV | 0.023955 | 0.084669 | 20 | Hawks Nest 132 kV | 1.3308 | 1.3308 | 1.3308 | 2.1538 | 19.5705 | 19.5706 | 19.5706 | 41.5795 | 1 |  |  | 1 | 0.0020363 | 140.8 | #REF! | 0 |  | 0 |  | 0 |  | 0
Haymarket 132 kV (Note s.) | 0 | 0 | 0 | Haymarket 132 kV | 8.041 | 8.0417 | 8.0417 | 2.6629 | 2.4765 | 2.4767 | 2.4767 | 0.74632 | 1 |  |  | 1 | 0 | 0 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Herons Creek (tee) 132 kV | 0.021949 | 0.033308 | 19 | Herons Creek | 1.6166 | 1.6167 | 1.6167 | 1.2412 | 19.0185 | 19.0205 | 19.0205 | 16.5316 | 1 |  |  | 1 | 0.0020148 | 66 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Holroyd 132 kV | 0 | 0 | 5 | Holroyd 132 kV | 17.9376 | 17.9397 | 17.9397 | 57.2802 | 5.2495 | 5.2501 | 5.2501 | 23.8624 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Ilford (tee) 132 kV (Note v.) | 0.03135 | 0.26698 | 34 | Ilford 132 kV | 1.4249 | 1.4254 | 1.4254 | 0.82521 | 33.5268 | 33.5381 | 33.5381 | 13.1682 | 1 |  |  | 1 | 0.020275 | 126.05 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Ingleburn 66 kV | 0.98312 | 0.77435 | 2 | Ingleburn 66 kV | 1.8801 | 1.8801 | 1.8801 | 5.4308 | 1.6385 | 1.6385 | 1.6385 | 4.8858 | 1 |  |  | 1 | 0.15849 | 122 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Inverell 66 kV | 0.033175 | 0.09921 | 9 | Inverell 66 kV | 2.8819 | 2.8831 | 2.8831 | 11.3167 | 9.418 | 9.422 | 9.422 | 39.5921 | 1 |  |  | 1 | 0.0025058 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Kempsey 33 kV | 0.032924 | 0.10728 | 10 | Kempsey 33 kV | 2.2038 | 2.2038 | 2.2038 | 5.2063 | 9.6027 | 9.6027 | 9.6027 | 23.4378 | 1 |  |  | 1 | 0.0045774 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Koolkhan 66 kV | 0 | 0 | 7 | Koolkhan 66 kV | 2.6198 | 2.6214 | 2.6214 | 7.3935 | 6.5577 | 6.5618 | 6.5618 | 18.6784 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Liddell 330 kV (33 kV supply via Mac Gen) | 0 | 0 | 6 | Liddell 330 kV (33 kV supply via Mac Gen) | 2.0474 | 2.0474 | 2.0474 | 0.28796 | 6.3387 | 6.3387 | 6.3387 | 1.0718 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Lismore 132 kV (Note s.) | 0 | 0 | 5 | Lismore 132 kV Note 3 | 4.264 | 4.2657 | 4.2657 | 3.373 | 4.8235 | 4.8255 | 4.8255 | 3.6504 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Liverpool 132 kV | 0.0073882 | 0.0020928 | 1 | Liverpool 132 kV | 2.8851 | 2.8851 | 2.8851 | 10.4513 | 0.90031 | 0.90033 | 0.90033 | 4.005 | 1 |  |  | 1 | 0.00052255 | 18.3 | #REF! | 0 |  | 17.8 |  | 0 |  | 0
Macarthur 132 kV (Note w.) | 0.21582 | 0.30794 | 1 | Macarthur 132 kV | 1.9759 | 1.9759 | 1.9759 | 4.7239 | 0.78007 | 0.78007 | 0.78007 | 3.7225 | 1 |  |  | 1 | 0.082722 | 40.7 | #REF! | 0 |  | 0.016667 |  | 0.016667 |  | 0
Macarthur 66 kV (Note w.) | 0.24552 | 0.35031 | 1 | Macarthur 66 kV | 0.43366 | 0.43366 | 0.43366 | 1.6656 | 0.28662 | 0.28662 | 0.28662 | 1.3125 | 1 |  |  | 1 | 0.2669 | 40.7 | #REF! | 0 |  | 0.016667 |  | 0.016667 |  | 0
Macksville 132 kV | 0.0035772 | 0.037321 | 23 | Macksville 132 kV | 1.7796 | 1.7799 | 1.7799 | 1.6928 | 23.2625 | 23.2663 | 23.2663 | 22.5551 | 1 |  |  | 1 | 0.0016547 | 52.5 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Manildra 132 kV | 0.016705 | 0.11882 | 13 | Manildra 132 kV | 1.118 | 1.1181 | 1.1181 | 0.68633 | 13.1528 | 13.1547 | 13.1547 | 5.1104 | 1 |  |  | 1 | 0.02325 | 82.1 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Marulan 132 kV | 0.2902 | 0.21893 | 66 | Marulan 132 kV | 7.2336 | 7.2336 | 7.2336 | 10.1576 | 5.9098 | 5.9098 | 5.9098 | 9.5976 | 1 |  |  | 1 | 0.022811 | 0 | #REF! | 0 |  | 0 |  | 0.016667 |  | 0
Molong 66 kV | 0 | 0 | 16 | Molong 66 kV | 0.6913 | 0.69164 | 0.69164 | 1.5819 | 16.2658 | 16.2739 | 16.2739 | 45.3928 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Moree 66 kV | 0.34918 | 1.0686 | 5 | Moree 66 kV | 1.5674 | 1.5675 | 1.5675 | 1.0912 | 4.7281 | 4.7284 | 4.7284 | 4.5754 | 1 |  |  | 1 | 0.23355 | 143 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Morven (tee) 132 kV | 31.7816 | 40.8207 | 20 | Morven 132 kV | 1.3308 | 1.3308 | 1.3308 | 1.7704 | 19.5705 | 19.5706 | 19.5706 | 32.355 | 0 |  |  | 0 | 1.2616 | 106.2 | #REF! | 23.5 |  | 0 |  | 0 |  | 0
Mount Piper 66 kV (Note v.) | 0.044173 | 0.10707 | 9 | Mount Piper 66 kV | 3.3622 | 3.3637 | 3.3637 | 6.2262 | 9.418 | 9.422 | 9.422 | 18.1787 | 1 |  |  | 1 | 0.0058898 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Mudgee (tee) 132 kV | 118.2555 | 661.56 | 3 | Mudgee 132 kV | 0.52864 | 0.52864 | 0.52864 | 2.2316 | 2.8269 | 2.827 | 2.827 | 13.4757 | 0 |  |  | 0 | 49.0929 | 126.05 | #REF! | 23.5 |  | 0 |  | 0 |  | 0
Munmorah 132 kV (Note x.) | 0 | 0 | 11 | Munmorah 132 kV | 11.1424 | 11.1427 | 11.1427 | 15.1367 | 10.7448 | 10.7452 | 10.7452 | 19.5683 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 84.2 |  | 0
Munmorah 33 kV (Note x.) | #DIV/0! | #DIV/0! | 0 | Munmorah 330 kV (via old Power Stn Txs) | 4.903 | 4.9034 | 4.9034 | 10.4329 | 4.7281 | 4.7284 | 4.7284 | 11.6612 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Munyang 33 kV | 0.010474 | 0.11591 | 9 | Munyang 33 kV | 3.1221 | 3.1234 | 3.1234 | 1.087 | 9.418 | 9.422 | 9.422 | 190.7062 | 1 |  |  | 1 | 0.00060779 | 78 | #REF! | 0.016667 |  | 23.5 |  | 0 |  | 30.5
Murrumbateman 132 kV | 0.38313 | 9.0569 | 20 | Murrumbateman 132 kV | 0.9981 | 0.9981 | 0.9981 | 1.6136 | 19.5705 | 19.5706 | 19.5706 | 48.8967 | 1 |  |  | 1 | 0.18523 | 37.1 | #REF! | 1 |  | 0 |  | 0 |  | 0
Murrumburrah 66 kV | 0.17079 | 0.53043 | 5 | Murrumburrah 66 kV | 1.6076 | 1.6077 | 1.6077 | 5.8505 | 4.7281 | 4.7284 | 4.7284 | 18.6044 | 1 |  |  | 1 | 0.028511 | 112.5 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Muswellbrook 132 kV | 4.035 | 1.4866 | 5 | Muswellbrook 132 kV | 9.8864 | 9.8871 | 9.8871 | 5.577 | 4.7281 | 4.7284 | 4.7284 | 2.8866 | 1 |  |  | 1 | 0.51502 | 126.9 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Nambucca 66 kV | 0.009668 | 0.12021 | 23 | Nambucca 66 kV | 1.7796 | 1.7799 | 1.7799 | 3.0121 | 23.2625 | 23.2663 | 23.2663 | 64.7067 | 1 |  |  | 1 | 0.0018578 | 36.3 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Narrabri 66 kV | 0.052127 | 0.11387 | 2 | Narrabri 66 kV | 0.91398 | 0.91415 | 0.91415 | 1.6593 | 2.1084 | 2.1088 | 2.1088 | 4.0406 | 1 |  |  | 1 | 0.028183 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Newcastle 132 kV | 0 | 0 | 1 | Newcastle 132 kV | 0.99829 | 0.99869 | 0.99869 | 3.1213 | 0.25421 | 0.25431 | 0.25431 | 1.3362 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Orange North 132 kV | 0 | 0 | 6 | Orange North 132 kV | 7.208 | 2.7236 | 2.7236 | 11.866 | 5.5425 | 2.0942 | 2.0942 | 6.6999 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Orange 66 kV | 0.0012808 | 0.0021282 | 2 | Orange 66 kV | 1.2765 | 1.2765 | 1.2765 | 1.4704 | 2.4222 | 2.4222 | 2.4222 | 3.3616 | 1 |  |  | 1 | 0.00063308 | 0.6 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Panorama 66 kV | 0.17797 | 0.23375 | 5 | Panorama 66 kV | 2.974 | 2.9742 | 2.9742 | 2.6663 | 4.7281 | 4.7284 | 4.7284 | 4.8726 | 1 |  |  | 1 | 0.047973 | 57.1 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Parkes 132 kV | 0 | 0 | 15 | Parkes 132 kV | 4.0585 | 0.66894 | 0.66894 | 3.3507 | 14.4688 | 2.3848 | 2.3848 | 8.2952 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Parkes 66 kV | 0.02158 | 0.10981 | 13 | Parkes 66 kV | 2.6642 | 2.6659 | 2.6659 | 9.8352 | 12.5373 | 12.5454 | 12.5454 | 50.5058 | 1 |  |  | 1 | 0.0021742 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Port Macquarie 33 kV | 0.0014109 | 0.0021411 | 4 | Port Macquarie 33 kV | 2.2524 | 2.2528 | 2.2528 | 6.7078 | 4.015 | 4.0157 | 4.0157 | 13.8319 | 1 |  |  | 1 | 0.00015479 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Queanbeyan 132 kV (Note y.) | 0.013513 | 0.016789 | 0 | [16 empty] | 0 |  | 23.5 |  | 0 |  | 0
Queanbeyan 66 kV | #DIV/0! | #DIV/0! | 7 | Queanbeyan 66 kV | 3.9991 | 3.9995 | 3.9995 | 1.7867 | 6.8186 | 6.8192 | 6.8192 | 3.2619 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 57.5 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Raleigh 132 kV | 0.010454 | 0.10874 | 23 | Raleigh 132 kV | 1.9773 | 1.9776 | 1.9776 | 1.8918 | 23.2625 | 23.2662 | 23.2662 | 31.1838 | 1 |  |  | 1 | 0.0034869 | 84.5 | #REF! | 0 |  | 23.5 |  | 0 |  | 0
Regentville 132 kV | 2.8653 | 1.4063 | 5 | Regentville 132 kV | 11.3734 | 11.3742 | 11.3742 | 20.0677 | 4.7281 | 4.7284 | 4.7284 | 12.3126 | 1 |  |  | 1 | 0.11422 | 171 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Rookwood Road 132 kV | 183.3325 | 31.4556 | 0 | Rookwood Road 132 kV | 5.3888 | 5.3892 | 5.3892 | 1.7301 | 2.4765 | 2.4767 | 2.4767 | 0.77235 | 0 |  |  | 0 | 40.7272 | 15.5 | #REF! | 0 |  | 1128 |  | 0 |  | 0
Snowy Adit (tee) 132 kV | 0 | 0 | 19 | Snowy Adit 132 kV | 1.6166 | 1.6167 | 1.6167 | 2.6538 | 19.0185 | 19.0205 | 19.0205 | 51.3629 | 1 |  |  | 1 | 0 | 78 | #REF! | 0 |  | 0 |  | 0 |  | 0
Stroud 132 kV | 0 | 0 | 5 | Stroud 132 kV | 1.2057 | 1.2057 | 1.2057 | 4.2811 | 4.7281 | 4.7284 | 4.7284 | 20.4185 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Sydney East 132 kV | 0 | 0 | 1 | Sydney East 132 kV | 2.459 | 2.4591 | 2.4591 | 5.4936 | 0.41806 | 0.41808 | 0.41808 | 1.1895 | 1 |  |  | 1 | 0 | 22.3 | #REF! | 0 |  | 17.8 |  | 0 |  | 0
Sydney North 132 kV | 0 | 0 | 0 | Sydney North 132 kV | 1.085 | 1.0854 | 1.0854 | 2.4198 | 0.1392 | 0.13926 | 0.13926 | 0.33438 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Sydney South 132 kV | 0 | 0 | 0 | Sydney South 132 kV | 1.1822 | 1.1828 | 1.1828 | 2.4255 | 0.14955 | 0.14963 | 0.14963 | 0.26592 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Sydney West 132 kV | 0 | 0 | 1 | Sydney West 132 kV | 7.5954 | 7.5967 | 7.5967 | 8.3479 | 0.7075 | 0.70762 | 0.70762 | 0.98326 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Tamworth 66 kV | 0.098999 | 0.098582 | 4 | Tamworth 66 kV | 3.968 | 3.9683 | 3.9683 | 3.3204 | 3.99 | 3.9903 | 3.9903 | 3.7783 | 1 |  |  | 1 | 0.026091 | 3 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Taree 33 kV | 0.04542 | 0.19291 | 13 | Taree 33 kV | 2.5576 | 2.5593 | 2.5593 | 7.4524 | 12.5373 | 12.5454 | 12.5454 | 39.6402 | 1 |  |  | 1 | 0.0048666 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Taree 66 kV | 0.024956 | 0.042234 | 9 | Taree 66 kV | 3.9226 | 3.9243 | 3.9243 | 1.3979 | 9.418 | 9.422 | 9.422 | 3.367 | 1 |  |  | 1 | 0.012543 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Tenterfield 22 kV | 0.041614 | 0.69876 | 23 | Tenterfield 22 kV | 1.1864 | 1.1866 | 1.1866 | 3.6623 | 23.2625 | 23.2663 | 23.2663 | 78.6751 | 1 |  |  | 1 | 0.0088816 | 124 | #REF! | 0 |  | 23.5 |  | 0 |  | 30.5
Tomago132 | 0 | 0 | 17 | Tomago 132 Note 3 | 32.4598 | 32.4604 | 32.4604 | 41.1087 | 16.676 | 16.6763 | 16.6763 | 12.1259 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Tomago 330 kV | 0 | 0 | 6 | Tomago 330 kV | 49.93 | 49.9721 | 49.9721 | 207.6667 | 6.2491 | 6.2543 | 6.2543 | 13.3071 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Tuggerah 132 kV | 3.0514 | 1.5371 | 5 | Tuggerah 132 kV | 8.0779 | 8.0785 | 8.0785 | 16.082 | 4.7281 | 4.7284 | 4.7284 | 12.3026 | 1 |  |  | 1 | 0.12494 | 64.6 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Tumut 66 kV | 0.046024 | 0.12083 | 5 | Tumut 66 kV | 1.5272 | 1.5273 | 1.5273 | 3.9006 | 4.7281 | 4.7284 | 4.7284 | 12.3191 | 1 |  |  | 1 | 0.0098083 | 52.7 | #REF! | 0 |  | 17.8 |  | 0 |  | 30.5
Vales Point 132 kV | 1.3444 | 1.4556 | 66 | Vales Pt 132 kV | 4.2778 | 4.2806 | 4.2806 | 1.2229 | 5.9208 | 5.9248 | 5.9248 | 2.0051 | 0 |  |  | 1 | 0.72597 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 84.2
Vineyard 132 kV | 0.048673 | 0.025519 | 4 | Vineyard 132 kV | 16.8556 | 16.8569 | 16.8569 | 2.0295 | 3.99 | 3.9903 | 3.9903 | 0.80316 | 1 |  |  | 1 | 0.031773 | 109.4 | #REF! | 0 |  | 17.8 |  | 0 |  | 0
Wagga 66 kV | 0.0013026 | 0.0095069 | 4 | Wagga 66 kV | 3.2763 | 3.2768 | 3.2768 | 14.943 | 4.015 | 4.0157 | 4.0157 | 32.5437 | 1 |  |  | 1 | 0.00029213 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Wagga North 132 kV | 0 | 0 | 5 | Wagga North 132 kV | 2.27 | 3.0528 | 3.0528 | 2.7596 | 4.451 | 5.9859 | 5.9859 | 4.1848 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Wagga North 66 kV | 0.014923 | 0.10892 | 16 | Wagga North 66 kV | 3.733 | 3.7348 | 3.7348 | 5.4067 | 16.2658 | 16.2739 | 16.2739 | 41.8477 | 1 |  |  | 1 | 0.0026027 | 0 | #REF! | 0 |  | 0 |  | 0.016667 |  | 0
Wallerawang 132 kV (Note aa.) | 0 | 0 | 5 | Wallerawang 132 kV Note 3 | 4.551 | 4.5529 | 4.5529 | 11.8764 | 4.8235 | 4.8255 | 4.8255 | 25.6416 | 1 |  |  | 1 | 0 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 0
Wallerawang 66 kV (Note aa.) | 0.02574 | 0.08505 | 5 | Wallerawang 66 kV | 1.2057 | 1.2057 | 1.2057 | 0.84687 | 4.7281 | 4.7284 | 4.7284 | 30.8889 | 1 |  |  | 1 | 0.0027534 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Waratah West 132 kV | 2.4981 | 1.1824 |  | Waratah West 132 kV | 6.2694 | 6.2699 | 6.2699 | 3.3728 | 4.7281 | 4.7284 | 4.7284 | 2.6067 | 1 |  |  | 1 | 0.45358 | 17.8 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Wellington 132 kV | 3.4504 | 1.9903 |  | Wellington 132 kV Note 3 | 3.2553 | 5.7025 | 5.7025 | 7.982 | 2.201 | 3.8556 | 3.8556 | 5.1201 | 1 |  |  | 1 | 0.38872 | 171 | #REF! | 0 |  | 17.8 |  | 0 |  | 84.2
Wellington Town (tee) 132 kV | 0.00531 | 0.20023 |  | Wellington Town | 0.96416 | 0.96416 | 0.96416 | 4.9655 | 9.4526 | 9.4525 | 9.4525 | 68.0114 | 1 |  |  | 1 | 0.0029441 | 66.3 | #REF! | 0.016667 |  | 0 |  | 0 |  | 0
Williamsdale 132 kV | 184.8609 | 33.9937 |  | Williamsdale 132 kV Note 3 | 2.5851 | 2.5853 | 2.5853 | 8.1546 | 1.6351 | 1.6352 | 1.6352 | 4.9422 | 0 |  |  | 0 | 6.8783 | 48.6 | #REF! | 17.8 |  | 0 |  | 0 |  | 84.2
Yanco 33 kV | 0.033706 | 0.091856 |  | Yanco 33 kV | 1.9124 | 1.9137 | 1.9137 | 13.4332 | 5.9208 | 5.9248 | 5.9248 | 40.4451 | 1 |  |  | 1 | 0.0022711 | 0 | #REF! | 0 |  | 0 |  | 0 |  | 30.5
Yass 132 kV (Note z.) | #DIV/0! | #DIV/0! |  | Yass 132 kV | 1.5988 | 1.3403 | 1.3403 | 1.2984 | 14.4688 | 12.1299 | 12.1299 | 17.6257 | #DIV/0! |  |  | #DIV/0! | #DIV/0! | 0 | #REF! | 0 |  | 0 |  | 0 |  | 84.2
Yass 66 kV | 0.0151 | 0.13742 |  | Yass 66 kV | 2.1015 | 2.1018 | 2.1018 | 2.1894 | 19.0185 | 19.0205 | 19.0205 | 21.4651 | 1 |  |  | 1 | 0.0064022 | 0 | #REF! | 0 |  | 0 |  | 0.016667 |  | 0

## full_summary
| DR | out23_0 | _input0 | basecase | base_bsp96LDC | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130
opex_capital_ratio |  |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
transformer_cost_multiplier |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
line_cost_multiplier |  |  |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
transformer_life_in_yrs |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 28 | 52 | 40 | 40 | 40 | 40 | 40 | 40
oh_line_life_in_yrs |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 65 | 50 | 50 | 50 | 50 | 50 | 50
ug_cable_life_in_yrs |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 31.5 | 58.5 | 45 | 45 | 45 | 45 | 45 | 45
discount_rate |  |  |  | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.047 | 0.064 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056
capital_efficiency_factor |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
failures_per_transformer_per_annum |  |  |  | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.005013 | 0.006127 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557 | 0.00557
failures_per_annum_per_100km_oh_line |  |  |  | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2611 | 0.3191 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901 | 0.2901
failures_per_annum_per_100km_ug_cable |  |  |  | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0535 | 0.0654 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595 | 0.0595
coef_for_transformer_cost_function_coef*MVA^exp |  |  |  | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944 | 0.0944
exponent_for_transformer_cost_function |  |  |  | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398
coef_for_line_cost_function_coef*MVA^exp |  |  |  | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0248 | 0.0173 | 0.0322 | 0.0248 | 0.0248
exponent_for_line_cost_function |  |  |  | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.6398 | 0.4483 | 0.8325
cost_multiplier_underground_cables |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 5 | 25 | 15 | 15 | 15 | 15
max_hrs_to_replace/repair_transformer |  |  |  | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351 | 15351
max_hrs_to_repair_OH_line |  |  |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
max_hrs_to_repair_cable |  |  |  | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016
Minutes EUE include allowance for non-catastrophic transformer failure
N-1 EUE (mins @ avg demand) | DR | out23_0 | _input0 | basecase | base_bsp96LDC | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130
Albury 132 kV | 4.015 | 4.0157 | 4.0157 | 13.335 | 13.335 | 13.335 | 22.7271 | 0.76773 | 9.2853 | 17.4268 | 9.3345 | 17.3355 | 13.335 | 13.335 | 11.9809 | 14.6938 | 13.335 | 13.335 | 13.335 | 13.335 | 0.76773 | 22.7271 | 0.76773 | 22.7271 | x
ANM 132 kV | 26.7347 | 26.745 | 26.745 | 5.4189 | 5.4189 | 5.4189 | 7.0163 | 5.4189 | 4.5336 | 7.1232 | 4.9114 | 7.0445 | 5.4189 | 5.4189 | 6.1531 | 5.9827 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189 | 5.4189
Armidale 66 kV | 4.9289 | 4.9289 | 4.9289 | 6.446 | 6.446 | 6.446 | 6.446 | 6.446 | 5.5864 | 6.2613 | 4.9003 | 7.9917 | 6.446 | 6.446 | 5.8582 | 7.0499 | 6.446 | 6.446 | 6.446 | 6.446 | 6.446 | 6.446 | 6.446 | 23.1725
Balranald 22 kV | 72.6404 | 72.6556 | 72.6556 | 114.0826 | 114.0826 | 114.0826 | 430.587 | 114.0826 | 83.3381 | 144.827 | 304.4707 | 145.2474 | 114.0826 | 430.587 | 388.5626 | 124.4674 | 114.0826 | 114.0826 | 114.0826 | 114.0826 | 114.0826 | 430.587 | 114.0826 | 430.587
Beaconsfield 132 kV | 2.4765 | 2.4767 | 2.4767 | 1.6213 | 1.6213 | 3.6467 | 1.6213 | 1.6213 | 1.6079 | 1.6345 | 2.7298 | 1.6459 | 1.6213 | 3.2401 | 3.0685 | 1.6295 | 3.2401 | 1.6213 | 1.6213 | 3.2401 | 1.6213 | 3.2401 | 1.6213 | 3.2401
Beryl 66 kV | 4.7281 | 4.7284 | 4.7284 | 4.6376 | 4.6376 | 4.6376 | 18.5697 | 4.6376 | 3.8849 | 5.642 | 13.3732 | 5.6545 | 4.6376 | 18.5697 | 16.827 | 4.9922 | 18.5697 | 4.6376 | 4.6376 | 4.6376 | 4.6376 | 18.5697 | 4.6376 | 18.5697
Boambee South 132 kV | 4.7281 | 4.7284 | 4.7284 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 11.9762 | 22.3372 | 12.002 | 22.2894 | 17.1457 | 17.1457 | 15.4207 | 18.8731 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 17.1457 | 3.7495 | 17.1457
Boggabri East | 38.7065 | 38.7103 | 38.7103 | 115.7279 | 115.7279 | 115.7279 | 326.509 | 115.7279 | 86.2351 | 145.2723 | 232.932 | 146.0705 | 115.7279 | 326.509 | 295.2395 | 125.8717 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 326.509 | 115.7279 | 326.509
Boggabri North | 38.7065 | 38.7104 | 38.7104 | 115.7279 | 115.7279 | 115.7279 | 211.6939 | 115.7279 | 86.2351 | 145.2723 | 85.3854 | 146.0706 | 115.7279 | 115.7279 | 105.5903 | 125.8716 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 115.7279 | 211.6939
Brandy Hill 132 kV | 13.1528 | 13.1547 | 13.1547 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 5.2844 | 8.8066 | 5.3924 | 8.5632 | 6.9778 | 6.9778 | 6.3719 | 7.601 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 6.9778 | 6.9778
Broken Hill 22 kV | 4.8071 | 4.8071 | 4.8071 | 13.8431 | 13.8431 | 13.8431 | 39.7256 | 13.8431 | 9.9821 | 17.704 | 28.0355 | 17.7685 | 13.8431 | 39.7256 | 35.7624 | 15.172 | 13.8431 | 13.8431 | 13.8431 | 13.8431 | 13.8431 | 39.7256 | 13.8431 | 39.7256
Broken Hill 220 kV | 252 | 4.7696 | 4.7696 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 3.0326 | 5.632 | 3.0326 | 5.632 | 4.3323 | 4.3323 | 3.8992 | 4.7654 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323 | 4.3323
Canberra 132 kV Note 3 | 1.9889 | 1.989 | 1.989 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.6695 | 2.2691 | 1.5915 | 2.3345 | 1.963 | 1.963 | 1.8326 | 2.0949 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963
Casino 132 kV | 2.8269 | 2.8269 | 2.8269 | 6.272 | 6.272 | 6.272 | 15.2833 | 6.272 | 4.3904 | 8.1536 | 10.6984 | 8.1536 | 6.272 | 6.272 | 13.7556 | 6.899 | 6.272 | 6.272 | 6.272 | 6.272 | 6.272 | 15.2833 | 6.272 | 15.2833
Coffs Harbour 66 kV | 5.8636 | 5.8636 | 5.8636 | 9.3239 | 9.3239 | 9.3239 | 11.6996 | 7.3442 | 10.1465 | 7.6818 | 9.9707 | 7.7665 | 9.3239 | 9.3239 | 8.9514 | 9.704 | 9.3239 | 9.3239 | 9.3239 | 9.3239 | 9.3239 | 9.3239 | 9.3239 | 9.3239
Coleambally 132 kV | 13.1528 | 13.1548 | 13.1548 | 31.4392 | 31.4392 | 31.4392 | 49.4602 | 31.4392 | 21.9776 | 40.9265 | 34.622 | 40.871 | 31.4392 | 49.4602 | 44.4977 | 34.5977 | 49.4602 | 31.4392 | 31.4392 | 31.4392 | 31.4392 | 49.4602 | 31.4392 | 49.4602
Cooma 11 kV | 9.609 | 9.617 | 9.617 | 27.8429 | 27.8429 | 27.8429 | 37.586 | 8.4102 | 28.2676 | 23.7785 | 28.1049 | 23.8461 | 27.8429 | 27.8429 | 25.6394 | 30.0505 | 27.8429 | 27.8429 | 27.8429 | 27.8429 | 17.1609 | 27.8429 | 17.1609 | 27.8429
Cooma 66 kV | 9.609 | 9.617 | 9.617 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 19.1604 | 34.9069 | 18.909 | 35.1168 | 27.0129 | 27.0129 | 24.2908 | 29.7397 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129 | 27.0129
Cooma 132 kV | 14.4688 | 3.8556 | 3.8556 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 7.5404 | 14.0859 | 7.5626 | 14.0448 | 10.8037 | 10.8037 | 9.7142 | 11.8953 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037 | 10.8037
Cowra 66 kV | 12.5373 | 12.5454 | 12.5454 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 20.125 | 29.8198 | 19.1694 | 30.7218 | 24.9456 | 24.9456 | 22.9925 | 26.905 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 24.9456 | 24.9456
Dapto 132 kV | 1.5945 | 1.5949 | 1.5949 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.0428 | 4.8684 | 3.0485 | 4.8429 | 3.9457 | 3.9457 | 3.6334 | 4.261 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.9457 | 3.9457
Darlington Point 132 kV Note 3 | 12.5525 | 12.563 | 12.563 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.2598 | 4.5609 | 3.2432 | 4.5775 | 3.9104 | 3.9104 | 3.688 | 4.1327 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.9104 | 3.9104
Deniliquin 66 kV | 4.7281 | 4.7284 | 4.7284 | 18.6678 | 18.6678 | 18.6678 | 18.6678 | 4.6938 | 13.5552 | 23.8026 | 13.4078 | 5.7616 | 4.6938 | 18.6678 | 16.9037 | 5.1136 | 18.6678 | 18.6678 | 18.6678 | 18.6678 | 4.6938 | 18.6678 | 4.6938 | 18.6678
Dorrigo 132 kV | 33.5268 | 33.538 | 33.538 | 40.3084 | 40.3084 | 40.3084 | 204.7316 | 34.9848 | 24.4897 | 52.4013 | 24.4897 | 52.4013 | 40.3084 | 40.3084 | 36.2792 | 44.3381 | 40.3084 | 40.3084 | 40.3084 | 40.3084 | 34.9848 | 40.3084 | 34.9848 | 40.3084
Finley 132 kV | 14.4688 | 3.8556 | 3.8556 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 11.8553 | 22.1131 | 11.8811 | 22.0649 | 16.973 | 16.973 | 15.2652 | 18.6833 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 16.973 | 3.4508 | 16.973
Finley 66 kV | 4.7281 | 4.7284 | 4.7284 | 11.8254 | 11.8254 | 11.8254 | 36.1521 | 3.5084 | 16.1281 | 15.0474 | 25.562 | 15.1175 | 11.8254 | 11.8254 | 23.669 | 12.9326 | 11.8254 | 11.8254 | 11.8254 | 11.8254 | 3.5084 | 26.2182 | 3.5084 | 26.2182
Forbes 66 kV | 4.7281 | 4.7284 | 4.7284 | 18.3068 | 18.3068 | 18.3068 | 18.3068 | 4.4813 | 13.2885 | 23.3469 | 13.1434 | 23.4701 | 18.3068 | 18.3068 | 16.575 | 20.041 | 18.3068 | 18.3068 | 18.3068 | 18.3068 | 4.4813 | 18.3068 | 4.4813 | 18.3068
Gadara (132 kV & 11 kV) | 29.3764 | 29.3783 | 29.3783 | 12.6923 | 12.6923 | 12.6923 | 20.3855 | 12.6923 | 9.4235 | 15.9793 | 9.3509 | 16.0337 | 12.6923 | 12.6923 | 11.5697 | 13.8169 | 12.6923 | 12.6923 | 12.6923 | 12.6923 | 12.6923 | 12.6923 | 12.6923 | 149.441
Glen Innes 66 kV | 12.5373 | 12.5454 | 12.5454 | 42.0547 | 42.0547 | 42.0547 | 61.6619 | 42.0547 | 33.9454 | 50.2008 | 47.0617 | 50.7726 | 42.0547 | 61.6619 | 56.7602 | 44.9833 | 61.6619 | 42.0547 | 42.0547 | 42.0547 | 31.2116 | 61.6619 | 42.0547 | 61.6619
Griffith 33 kV | 3.99 | 3.9903 | 3.9903 | 11.056 | 11.056 | 11.056 | 11.056 | 11.056 | 7.8718 | 14.2595 | 7.8413 | 14.2707 | 11.056 | 11.056 | 9.975 | 12.1392 | 11.056 | 11.056 | 11.056 | 11.056 | 11.056 | 11.056 | 2.3721 | 24.5357
Gunnedah 66 kV | 4.7281 | 4.7284 | 4.7284 | 18.8348 | 18.8348 | 18.8348 | 18.8348 | 4.2001 | 13.6457 | 24.046 | 13.4927 | 24.177 | 18.8348 | 18.8348 | 17.0434 | 20.6288 | 18.8348 | 18.8348 | 18.8348 | 18.8348 | 4.2001 | 18.8348 | 4.2001 | 18.8348
Hawks Nest 132 kV | 19.5705 | 19.5706 | 19.5706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 29.1058 | 54.0535 | 29.1058 | 54.0535 | 41.5795 | 41.5795 | 37.423 | 45.7361 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 35.5674
Haymarket 132 kV | 2.4765 | 2.4767 | 2.4767 | 0.74632 | 0.74632 | 3.2573 | 0.74632 | 0.74632 | 0.733 | 0.75963 | 2.0265 | 0.76449 | 0.74632 | 0.74632 | 0.74019 | 0.75238 | 0.74632 | 0.74632 | 0.74632 | 2.6011 | 0.74632 | 2.6011 | 0.74632 | 7.2537
Herons Creek | 19.0185 | 19.0205 | 19.0205 | 16.5316 | 16.5316 | 16.5316 | 39.3218 | 5.9933 | 27.5251 | 7.7913 | 27.5251 | 7.7913 | 16.5316 | 27.4004 | 24.6613 | 18.1842 | 27.4004 | 16.5316 | 16.5316 | 16.5316 | 16.5316 | 27.4004 | 16.5316 | 27.4004
Holroyd 132 kV | 5.2495 | 5.2501 | 5.2501 | 23.8624 | 23.8624 | 23.8624 | 23.8624 | 23.8624 | 17.292 | 30.4814 | 16.7037 | 31.0212 | 23.8624 | 23.8624 | 21.4326 | 26.261 | 23.8624 | 23.8624 | 0.86851 | 23.8624 | 20.1176 | 23.8624 | 0.86851 | 23.8624
Ilford 132 kV | 33.5268 | 33.5381 | 33.5381 | 13.1682 | 13.1682 | 13.1682 | 33.7234 | 13.1682 | 18.4356 | 17.1188 | 18.4356 | 17.1188 | 13.1682 | 33.7234 | 30.3522 | 14.4846 | 26.3365 | 13.1682 | 13.1682 | 13.1682 | 13.1682 | 33.7234 | 13.1682 | 33.7234
Ingleburn 66 kV | 1.6385 | 1.6385 | 1.6385 | 4.8858 | 4.8858 | 4.8858 | 4.8858 | 1.3362 | 1.3294 | 5.9291 | 3.6583 | 1.4988 | 4.8858 | 4.8858 | 4.476 | 5.2957 | 4.8858 | 4.8858 | 4.8858 | 4.8858 | 1.3362 | 4.8858 | 1.3362 | 4.8858
Inverell 66 kV | 9.418 | 9.422 | 9.422 | 39.5921 | 39.5921 | 39.5921 | 39.5921 | 27.8899 | 25.1921 | 47.1217 | 30.5052 | 37.5861 | 27.8899 | 39.5921 | 36.5273 | 33.2685 | 39.5921 | 31.0591 | 39.5921 | 39.5921 | 27.8899 | 39.5921 | 27.8899 | 39.5921
Kempsey 33 kV | 9.6027 | 9.6027 | 9.6027 | 23.4378 | 23.4378 | 23.4378 | 52.7384 | 23.4378 | 21.9855 | 24.9579 | 21.333 | 25.5425 | 23.4378 | 23.4378 | 22.7016 | 24.1817 | 23.4378 | 23.4378 | 23.4378 | 23.4378 | 23.4378 | 52.7384 | 23.4378 | 52.7384
Koolkhan 66 kV | 6.5577 | 6.5618 | 6.5618 | 18.6784 | 18.6784 | 18.6784 | 21.5399 | 16.2938 | 15.9967 | 20.3195 | 15.8858 | 20.3741 | 18.6784 | 18.6784 | 17.0577 | 20.3041 | 18.6784 | 18.6784 | 18.6784 | 18.6784 | 18.6784 | 18.6784 | 3.5411 | 18.6784
Liddell 330 kV (33 kV supply via Mac Gen) | 6.3387 | 6.3387 | 6.3387 | 1.0718 | 1.0718 | 1.0718 | 6.7915 | 1.0718 | 4.5528 | 1.4322 | 4.754 | 1.3934 | 1.0718 | 1.8274 | 1.5677 | 1.1899 | 1.8274 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 1.0718
Lismore 132 kV Note 3 | 4.8235 | 4.8255 | 4.8255 | 3.6504 | 3.6504 | 3.6504 | 19.6245 | 3.6504 | 3.0573 | 4.4422 | 3.12 | 4.452 | 3.6504 | 4.0377 | 3.6869 | 3.93 | 4.0377 | 3.6504 | 3.6504 | 3.6504 | 3.6504 | 3.6504 | 3.6504 | 19.6245
Liverpool 132 kV | 0.90031 | 0.90033 | 0.90033 | 4.005 | 4.005 | 4.005 | 8.9853 | 1.4166 | 3.1411 | 3.8698 | 3.1294 | 3.8746 | 3.2311 | 4.005 | 3.7113 | 3.4478 | 4.005 | 3.2311 | 4.005 | 4.005 | 1.4166 | 4.005 | 1.4166 | 8.3134
Macarthur 132 kV | 0.78007 | 0.78007 | 0.78007 | 3.7225 | 3.7225 | 3.7225 | 6.743 | 1.4437 | 1.2729 | 6.9676 | 2.8598 | 1.6228 | 3.7225 | 3.7225 | 3.4174 | 4.0316 | 6.743 | 3.7225 | 3.7225 | 3.7225 | 1.4437 | 6.743 | 1.4437 | 12.1171
Macarthur 66 kV | 0.28662 | 0.28662 | 0.28662 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.1811 | 1.4439 | 1.1727 | 1.4523 | 1.3125 | 1.3125 | 1.2659 | 1.3591 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 1.3125 | 5.4914
Macksville 132 kV | 23.2625 | 23.2663 | 23.2663 | 22.5551 | 22.5551 | 22.5551 | 38.3498 | 10.6532 | 26.8152 | 29.375 | 26.8448 | 29.3217 | 22.5551 | 22.5551 | 34.5034 | 24.8249 | 22.5551 | 22.5551 | 22.5551 | 22.5551 | 10.6532 | 22.5551 | 10.6532 | 22.5551
Manildra 132 kV | 13.1528 | 13.1547 | 13.1547 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 3.4196 | 6.9365 | 3.5773 | 6.6436 | 5.1104 | 5.1104 | 4.532 | 5.7039 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104 | 5.1104
Marulan 132 kV | 5.9098 | 5.9098 | 5.9098 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.358 | 9.8497 | 6.9723 | 12.2229 | 9.5976 | 9.5976 | 8.7163 | 10.4803 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.5976 | 9.5976
Molong 66 kV | 16.2658 | 16.2739 | 16.2739 | 45.3928 | 45.3928 | 45.3928 | 72.3911 | 45.3928 | 37.1879 | 53.633 | 53.7337 | 55.9509 | 45.3928 | 72.3911 | 66.1352 | 48.9329 | 72.3911 | 45.3928 | 45.3928 | 45.3928 | 45.3928 | 72.3911 | 45.3928 | 72.3911
Moree 66 kV | 4.7281 | 4.7284 | 4.7284 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 3.4672 | 5.7723 | 3.538 | 5.6128 | 4.5754 | 4.5754 | 4.1789 | 4.9832 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 4.5754 | 4.5754
Morven 132 kV | 19.5705 | 19.5706 | 19.5706 | 32.355 | 32.355 | 32.355 | 32.355 | 19.8272 | 22.6485 | 25.7753 | 22.6485 | 25.7753 | 32.355 | 32.355 | 29.1207 | 35.5895 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355 | 32.355
Mount Piper 66 kV | 9.418 | 9.422 | 9.422 | 18.1787 | 18.1787 | 18.1787 | 18.1787 | 2.7648 | 14.0769 | 22.3255 | 13.0538 | 23.3037 | 18.1787 | 18.1787 | 16.4469 | 19.916 | 18.1787 | 18.1787 | 18.1787 | 18.1787 | 2.7648 | 18.1787 | 2.7648 | 18.1787
Mudgee 132 kV | 2.8269 | 2.827 | 2.827 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 9.433 | 17.5184 | 9.433 | 17.5184 | 13.4757 | 13.4757 | 12.1286 | 14.8228 | 13.4757 | 13.4757 | 13.4757 | 13.4757 | 2.1835 | 13.4757 | 2.1835 | 29.2212
Munmorah 132 kV | 10.7448 | 10.7452 | 10.7452 | 19.5683 | 19.5683 | 19.5683 | 19.5683 | 5.4143 | 4.8285 | 23.0852 | 13.9518 | 6.7846 | 5.4143 | 19.5683 | 17.6873 | 5.8998 | 19.5683 | 19.5683 | 19.5683 | 19.5683 | 5.4143 | 19.5683 | 5.4143 | 35.2257
Munmorah 330 kV (via old Power Stn Txs) | 4.7281 | 4.7284 | 4.7284 | 11.6612 | 11.6612 | 11.6612 | 11.6612 | 11.6612 | 8.4107 | 14.9313 | 8.3198 | 15.0026 | 11.6612 | 11.6612 | 10.5378 | 12.7868 | 11.6612 | 11.6612 | 11.6612 | 11.6612 | 2.1571 | 11.6612 | 2.1571 | 26.1046
Munyang 33 kV | 9.418 | 9.422 | 9.422 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 136.2291 | 245.1852 | 135.1466 | 246.2659 | 190.7062 | 190.7062 | 172.1922 | 209.222 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 190.7062 | 190.7062
Murrumbateman 132 kV | 19.5705 | 19.5706 | 19.5706 | 48.8967 | 48.8967 | 48.8967 | 208.3255 | 48.8967 | 34.2276 | 63.5658 | 50.8361 | 63.5658 | 48.8967 | 48.8967 | 44.0088 | 53.7845 | 48.8967 | 48.8967 | 48.8967 | 48.8967 | 48.8967 | 208.3255 | 48.8967 | 208.3255
Murrumburrah 66 kV | 4.7281 | 4.7284 | 4.7284 | 18.6044 | 18.6044 | 18.6044 | 18.6044 | 4.5585 | 13.5036 | 23.7272 | 13.3558 | 23.853 | 18.6044 | 18.6044 | 16.8442 | 20.3671 | 18.6044 | 18.6044 | 18.6044 | 18.6044 | 4.5585 | 18.6044 | 4.5585 | 18.6044
Muswellbrook 132 kV | 4.7281 | 4.7284 | 4.7284 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.4187 | 3.5113 | 2.2543 | 3.5189 | 2.8866 | 2.8866 | 2.6678 | 3.1071 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.8866 | 2.8866
Nambucca 66 kV | 23.2625 | 23.2663 | 23.2663 | 64.7067 | 64.7067 | 64.7067 | 64.7067 | 47.2175 | 48.9773 | 80.4665 | 48.5995 | 80.8139 | 64.7067 | 64.7067 | 59.3236 | 70.0931 | 64.7067 | 64.7067 | 64.7067 | 64.7067 | 47.2175 | 64.7067 | 47.2175 | 64.7067
Narrabri 66 kV | 2.1084 | 2.1088 | 2.1088 | 4.0406 | 4.0406 | 4.0406 | 16.0562 | 3.5394 | 3.2645 | 4.0715 | 3.1916 | 4.2381 | 4.0406 | 4.0406 | 3.7065 | 3.7797 | 4.0406 | 4.0406 | 4.0406 | 4.0406 | 4.0406 | 4.0406 | 4.0406 | 16.0562
Newcastle 132 kV | 0.25421 | 0.25431 | 0.25431 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.1993 | 1.48 | 0.98794 | 1.6845 | 1.3362 | 1.3362 | 1.2161 | 1.4573 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.3362 | 1.3362
Orange North 132 kV | 5.5425 | 2.0942 | 2.0942 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 5.4308 | 7.9833 | 5.3894 | 8.0105 | 6.6999 | 6.6999 | 6.2453 | 7.1585 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 6.6999 | 6.6999
Orange 66 kV | 2.4222 | 2.4222 | 2.4222 | 3.3616 | 3.3616 | 3.3616 | 3.3616 | 2.8272 | 2.7943 | 3.1345 | 2.6335 | 3.395 | 2.8272 | 3.3616 | 3.0638 | 3.0251 | 3.3616 | 3.3616 | 3.3616 | 3.3616 | 3.3616 | 3.3616 | 3.3616 | 3.3616
Panorama 66 kV | 4.7281 | 4.7284 | 4.7284 | 4.8726 | 4.8726 | 4.8726 | 12.2857 | 4.8726 | 4.08 | 5.9301 | 4.1637 | 5.9432 | 4.8726 | 5.3893 | 4.9209 | 5.2459 | 5.3893 | 4.8726 | 4.8726 | 4.8726 | 4.8726 | 12.2857 | 4.8726 | 12.2857
Parkes 132 kV | 14.4688 | 2.3848 | 2.3848 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 5.3602 | 11.6129 | 5.8067 | 10.7838 | 8.2952 | 8.2952 | 7.2747 | 9.3582 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952 | 8.2952
Parkes 66 kV | 12.5373 | 12.5454 | 12.5454 | 50.5058 | 50.5058 | 50.5058 | 50.5058 | 12.4113 | 39.1773 | 61.9102 | 37.7347 | 63.2768 | 50.5058 | 50.5058 | 46.2098 | 54.8107 | 50.5058 | 50.5058 | 50.5058 | 50.5058 | 16.1497 | 50.5058 | 16.1497 | 50.5058
Port Macquarie 33 kV | 4.015 | 4.0157 | 4.0157 | 13.8319 | 13.8319 | 13.8319 | 13.8319 | 13.8319 | 9.9626 | 17.7476 | 9.8774 | 17.7865 | 13.8319 | 13.8319 | 12.4906 | 15.1785 | 13.8319 | 13.8319 | 13.8319 | 13.8319 | 13.8319 | 13.8319 | 1.8907 | 13.8319
Queanbeyan 66 kV | 6.8186 | 6.8192 | 6.8192 | 3.2619 | 3.2619 | 3.2619 | 14.172 | 3.2619 | 2.6118 | 3.9121 | 10.2384 | 3.9226 | 3.2619 | 14.172 | 12.8194 | 3.4821 | 14.172 | 3.2619 | 3.2619 | 3.2619 | 3.2619 | 14.172 | 3.2619 | 14.172
Raleigh 132 kV | 23.2625 | 23.2662 | 23.2662 | 31.1838 | 31.1838 | 31.1838 | 47.7857 | 31.1838 | 33.4218 | 40.5893 | 33.45 | 40.5391 | 31.1838 | 31.1838 | 28.0549 | 34.3154 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838 | 31.1838
Regentville 132 kV | 4.7281 | 4.7284 | 4.7284 | 12.3126 | 12.3126 | 12.3126 | 19.5754 | 12.3126 | 8.7847 | 15.861 | 13.7617 | 15.9475 | 12.3126 | 12.3126 | 11.0909 | 13.5366 | 12.3126 | 12.3126 | 12.3126 | 12.3126 | 1.0699 | 19.5754 | 1.0699 | 19.5754
Rookwood Road 132 kV | 2.4765 | 2.4767 | 2.4767 | 0.77235 | 0.77235 | 5.1593 | 0.77235 | 0.77235 | 1.0479 | 0.79114 | 0.95865 | 0.79833 | 0.77235 | 0.77235 | 0.7613 | 0.78382 | 0.77235 | 0.77235 | 0.77235 | 4.5123 | 0.77235 | 4.5123 | 0.77235 | 4.5123
Snowy Adit 132 kV | 19.0185 | 19.0205 | 19.0205 | 51.3629 | 51.3629 | 51.3629 | 51.3629 | 28.338 | 35.9539 | 52.3841 | 35.9539 | 52.3841 | 51.3629 | 51.3629 | 46.2283 | 56.4974 | 51.3629 | 51.3629 | 51.3629 | 51.3629 | 40.2025 | 51.3629 | 40.2025 | 73.5542
Stroud 132 kV | 4.7281 | 4.7284 | 4.7284 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 14.233 | 26.6553 | 14.2929 | 26.544 | 20.4185 | 20.4185 | 18.3516 | 22.491 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185 | 20.4185
Sydney East 132 kV | 0.41806 | 0.41808 | 0.41808 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 0.96821 | 1.4256 | 0.98198 | 1.397 | 1.1895 | 1.1895 | 1.1129 | 1.2677 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 5.3205
Sydney North 132 kV | 0.1392 | 0.13926 | 0.13926 | 0.33438 | 0.33438 | 0.64226 | 0.33438 | 0.33438 | 0.32187 | 0.35242 | 0.29883 | 0.36993 | 0.33438 | 0.33438 | 0.32533 | 0.35274 | 0.33438 | 0.33438 | 0.33438 | 0.33438 | 0.33438 | 0.33438 | 0.33438 | 0.33438
Sydney South 132 kV | 0.14955 | 0.14963 | 0.14963 | 0.26592 | 0.26592 | 0.48825 | 0.26592 | 0.26592 | 0.25775 | 0.27945 | 0.23795 | 0.29388 | 0.26592 | 0.26592 | 0.25991 | 0.28083 | 0.26592 | 0.26592 | 0.26592 | 0.26592 | 0.26592 | 0.26592 | 0.26592 | 0.26592
Sydney West 132 kV | 0.7075 | 0.70762 | 0.70762 | 0.98326 | 0.98326 | 0.98326 | 0.98326 | 0.22491 | 0.18903 | 1.0246 | 0.71622 | 0.26445 | 0.98326 | 0.98326 | 0.89081 | 1.0765 | 0.98326 | 0.98326 | 0.98326 | 0.98326 | 0.22491 | 0.98326 | 0.22491 | 0.98326
Tamworth 66 kV | 3.99 | 3.9903 | 3.9903 | 3.7783 | 3.7783 | 3.7783 | 18.6729 | 3.7783 | 3.1658 | 4.596 | 3.2305 | 4.606 | 3.7783 | 3.7783 | 3.8159 | 4.067 | 3.7783 | 3.7783 | 3.7783 | 3.7783 | 3.7783 | 18.6729 | 3.7783 | 18.6729
Taree 33 kV | 12.5373 | 12.5454 | 12.5454 | 39.6402 | 39.6402 | 39.6402 | 39.6402 | 27.6281 | 31.6462 | 47.7009 | 30.1961 | 49.0843 | 39.6402 | 39.6402 | 36.4575 | 42.8308 | 39.6402 | 39.6402 | 39.6402 | 39.6402 | 27.6281 | 39.6402 | 27.6281 | 39.6402
Taree 66 kV | 9.418 | 9.422 | 9.422 | 3.367 | 3.367 | 3.367 | 28.3158 | 3.367 | 2.7644 | 3.3904 | 2.7054 | 4.0286 | 3.367 | 3.367 | 3.1067 | 3.6362 | 3.367 | 3.367 | 3.367 | 3.367 | 3.367 | 3.367 | 3.367 | 28.3158
Tenterfield 22 kV | 23.2625 | 23.2663 | 23.2663 | 78.6751 | 78.6751 | 78.6751 | 78.6751 | 42.4978 | 60.0802 | 73.4933 | 59.6809 | 50.639 | 42.4978 | 78.6751 | 72.3307 | 45.2222 | 78.6751 | 78.6751 | 78.6751 | 78.6751 | 42.4978 | 78.6751 | 42.4978 | 78.6751
Tomago 132 Note 3 | 16.676 | 16.6763 | 16.6763 | 12.1259 | 12.1259 | 12.1259 | 12.1259 | 12.1259 | 9.2688 | 15.0733 | 9.2501 | 15.0018 | 12.1259 | 12.1259 | 11.0928 | 13.1757 | 12.1259 | 12.1259 | 12.1259 | 12.1259 | 12.1259 | 12.1259 | 3.3687 | 12.1259
Tomago 330 kV | 6.2491 | 6.2543 | 6.2543 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 10.4494 | 16.2551 | 10.3238 | 16.2904 | 13.3071 | 13.3071 | 12.2086 | 14.4289 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 13.3071 | 13.3071
Tuggerah 132 kV | 4.7281 | 4.7284 | 4.7284 | 12.3026 | 12.3026 | 12.3026 | 12.3026 | 2.3855 | 8.9 | 15.7238 | 8.8043 | 15.8009 | 12.3026 | 12.3026 | 11.1275 | 13.4799 | 12.3026 | 12.3026 | 12.3026 | 12.3026 | 2.6389 | 12.3026 | 2.6389 | 26.9421
Tumut 66 kV | 4.7281 | 4.7284 | 4.7284 | 12.3191 | 12.3191 | 12.3191 | 24.1767 | 5.7296 | 4.3411 | 15.54 | 9.0425 | 7.0294 | 5.7296 | 12.3191 | 11.2182 | 6.2405 | 12.3191 | 12.3191 | 12.3191 | 12.3191 | 5.7296 | 12.3191 | 5.7296 | 24.1767
Vales Pt 132 kV | 5.9208 | 5.9248 | 5.9248 | 2.0051 | 2.0051 | 2.0051 | 29.7106 | 2.0051 | 3.2968 | 2.2754 | 20.9813 | 2.4227 | 2.0051 | 29.7106 | 26.7692 | 2.1683 | 29.7106 | 2.0051 | 2.0051 | 2.0051 | 2.0051 | 29.7106 | 2.0051 | 29.7106
Vineyard 132 kV | 3.99 | 3.9903 | 3.9903 | 0.80316 | 0.80316 | 0.80316 | 23.952 | 0.80316 | 1.2319 | 1.1031 | 16.8075 | 1.003 | 0.80316 | 23.952 | 21.5572 | 0.90036 | 23.952 | 0.80316 | 0.80316 | 0.80316 | 0.80316 | 23.952 | 0.80316 | 38.4058
Wagga 66 kV | 4.015 | 4.0157 | 4.0157 | 32.5437 | 32.5437 | 32.5437 | 32.5437 | 6.8919 | 24.9548 | 38.2061 | 24.4697 | 38.6312 | 32.5437 | 32.5437 | 29.8233 | 35.2709 | 32.5437 | 32.5437 | 32.5437 | 32.5437 | 9.3354 | 32.5437 | 9.3354 | 32.5437
Wagga North 132 kV | 4.451 | 5.9859 | 5.9859 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 3.2206 | 5.4712 | 2.9294 | 5.4403 | 4.1848 | 4.1848 | 3.7594 | 4.6119 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848 | 4.1848
Wagga North 66 kV | 16.2658 | 16.2739 | 16.2739 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 34.7146 | 49.016 | 32.3534 | 51.342 | 41.8477 | 41.8477 | 38.6661 | 45.0332 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 41.8477 | 41.8477
Wallerawang 132 kV Note 3 | 4.8235 | 4.8255 | 4.8255 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 18.4235 | 32.9051 | 17.9491 | 33.3341 | 25.6416 | 25.6416 | 23.0549 | 28.2336 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 25.6416 | 3.6113 | 25.6416
Wallerawang 66 kV | 4.7281 | 4.7284 | 4.7284 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 23.5667 | 38.2847 | 21.6222 | 40.1559 | 30.8889 | 30.8889 | 27.7612 | 34.0257 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889 | 30.8889
Waratah West 132 kV | 4.7281 | 4.7284 | 4.7284 | 2.6067 | 2.6067 | 2.6067 | 2.6067 | 2.3566 | 1.9746 | 2.8669 | 2.0152 | 3.1982 | 2.6067 | 2.6067 | 2.3805 | 2.5367 | 2.6067 | 2.6067 | 2.6067 | 2.6067 | 2.6067 | 2.6067 | 2.6067 | 22.8612
Wellington 132 kV Note 3 | 2.201 | 3.8556 | 3.8556 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 4.0222 | 6.2303 | 3.996 | 6.2442 | 5.1201 | 5.1201 | 4.7313 | 5.512 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 5.1201 | 18.7286
Wellington Town | 9.4526 | 9.4525 | 9.4525 | 68.0114 | 20.353 | 68.0114 | 68.0114 | 21.3512 | 47.608 | 88.4147 | 47.608 | 88.4147 | 68.0114 | 68.0114 | 61.2126 | 74.8102 | 68.0114 | 68.0114 | 68.0114 | 68.0114 | 21.3512 | 68.0114 | 12.5724 | 68.0114
Williamsdale 132 kV Note 3 | 1.6351 | 1.6352 | 1.6352 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.5203 | 5.3778 | 3.8181 | 6.0662 | 4.9422 | 4.9422 | 4.5596 | 5.3265 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.9422 | 4.9422
Yanco 33 kV | 5.9208 | 5.9248 | 5.9248 | 40.4451 | 40.4451 | 40.4451 | 40.4451 | 17.4119 | 18.481 | 46.2703 | 32.4426 | 18.5045 | 17.4119 | 40.4451 | 37.7381 | 17.8061 | 40.4451 | 40.4451 | 40.4451 | 40.4451 | 17.4119 | 40.4451 | 17.4119 | 40.4451
Yass 132 kV | 14.4688 | 12.1299 | 12.1299 | 17.6257 | 17.6257 | 17.6257 | 34.7614 | 3.3459 | 24.2236 | 4.5417 | 24.3331 | 4.3496 | 17.6257 | 17.6257 | 15.8183 | 19.4433 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257 | 17.6257
Yass 66 kV | 19.0185 | 19.0205 | 19.0205 | 21.4651 | 21.4651 | 21.4651 | 45.4607 | 21.4651 | 19.2587 | 23.7713 | 18.312 | 24.6181 | 21.4651 | 21.4651 | 20.3629 | 22.5786 | 21.4651 | 21.4651 | 21.4651 | 21.4651 | 21.4651 | 45.4607 | 21.4651 | 21.4651
|  |  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x

## grouped_bsp
N-1 EUE (MWh) | DR | out23_0 | _input0 | basecase | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130 |  |  | noncat tx failure EUE MWh
Canberra 132 kV Note 3 | 8.0808 | 8.0811 | 8.0811 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 3.7673 | 6.1581 | 3.4564 | 6.4191 | 4.9378 | 4.9378 | 4.4176 | 5.4638 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | 4.9378 | x |  | 2.8897
Williamsdale 132 kV Note 3 | 2.5851 | 2.5853 | 2.5853 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 5.4861 | 6.901 | 4.3275 | 8.0368 | 6.1822 | 6.1822 | 5.5509 | 6.8163 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | 6.1822 | x |  | 1.9724
Canberra group total MWh | 10.6659 | 10.6664 | 10.6664 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | 9.2534 | 13.0591 | 7.7839 | 14.4559 | 11.1199 | 11.1199 | 9.9685 | 12.2801 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | 11.1199 | x |  | 4.8621
Macarthur 132 kV | 1.9759 | 1.9759 | 1.9759 | 3.6496 | 3.6496 | 7.4825 | 0.7577 | 0.54092 | 7.7675 | 2.5547 | 0.98501 | 3.6496 | 3.6496 | 3.2623 | 4.0417 | 7.4825 | 3.6496 | 3.6496 | 3.6496 | 0.7577 | 7.4825 | 0.7577 | 14.3023 | x |  | 1.0743
Macarthur 66 kV | 0.43366 | 0.43366 | 0.43366 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.42454 | 0.75795 | 0.41387 | 0.76862 | 0.59124 | 0.59124 | 0.53214 | 0.65035 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 0.59124 | 5.8942 | x |  | 1.0743
Macarthur group total MWh | 2.4096 | 2.4096 | 2.4096 | 4.2408 | 4.2408 | 8.0738 | 1.3489 | 0.96546 | 8.5255 | 2.9686 | 1.7536 | 4.2408 | 4.2408 | 3.7945 | 4.6921 | 8.0738 | 4.2408 | 4.2408 | 4.2408 | 1.3489 | 8.0738 | 1.3489 | 20.1965 | x |  | 2.1487
Orange North 132 kV | 7.208 | 2.7236 | 2.7236 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 5.4891 | 10.0096 | 5.4157 | 10.0578 | 7.7367 | 7.7367 | 6.9316 | 8.5489 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | 7.7367 | x |  | 4.1293
Orange 66 kV | 1.2765 | 1.2765 | 1.2765 | 1.0615 | 1.0615 | 1.0615 | 0.82782 | 0.81341 | 0.9622 | 0.74308 | 1.0762 | 0.82782 | 1.0615 | 0.93129 | 0.91436 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | x |  | 0.40881
Orange group total MWh | 8.4845 | 4.0001 | 4.0001 | 8.7983 | 8.7983 | 8.7983 | 8.5646 | 6.3025 | 10.9718 | 6.1588 | 11.1339 | 8.5646 | 8.7983 | 7.8629 | 9.4633 | 8.7983 | 8.7983 | 8.7983 | 8.7983 | 8.7983 | 8.7983 | 8.7983 | 8.7983 | x |  | 4.5381
Taree 33 kV | 2.5576 | 2.5593 | 2.5593 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 4.4154 | 7.4337 | 4.1428 | 7.6938 | 5.9183 | 5.9183 | 5.3199 | 6.5181 | 5.9183 | 5.9183 | 5.9183 | 5.9183 | 3.66 | 5.9183 | 3.66 | 5.9183 | x |  | 1.5341
Taree 66 kV | 3.9226 | 3.9243 | 3.9243 | 0.91564 | 0.91564 | 11.2735 | 0.91564 | 0.66544 | 0.92535 | 0.64095 | 1.1903 | 0.91564 | 0.91564 | 0.80757 | 1.0274 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 0.91564 | 11.2735 | x |  | 0.48223
Taree group total MWh | 6.4802 | 6.4835 | 6.4835 | 6.8339 | 6.8339 | 17.1918 | 4.5756 | 5.0808 | 8.359 | 4.7837 | 8.8841 | 6.8339 | 6.8339 | 6.1275 | 7.5455 | 6.8339 | 6.8339 | 6.8339 | 6.8339 | 4.5756 | 6.8339 | 4.5756 | 17.1918 | x |  | 2.0163
Beaconsfield 132 kV | 6.5465 | 6.547 | 6.547 | 0.27224 | 6.9859 | 0.27224 | 0.27224 | 0.22815 | 0.31632 | 3.9466 | 0.35391 | 0.27224 | 5.638 | 5.0694 | 0.2995 | 5.638 | 0.27224 | 0.27224 | 5.638 | 0.27224 | 5.638 | 0.27224 | 5.638 |  |  | 5.1017
Haymarket 132 kV | 8.041 | 8.0417 | 8.0417 | 0.21612 | 9.1753 | 0.21612 | 0.21612 | 0.16862 | 0.26361 | 4.7839 | 0.28095 | 0.21612 | 0.21612 | 0.19424 | 0.23776 | 0.21612 | 0.21612 | 0.21612 | 6.8341 | 0.21612 | 6.8341 | 0.21612 | 23.4343 |  |  | 2.4467
Rookwood Road 132 kV | 5.3888 | 5.3892 | 5.3892 | 0.19399 | 10.0207 | 0.19399 | 0.19399 | 0.81115 | 0.23608 | 0.6113 | 0.25219 | 0.19399 | 0.19399 | 0.16924 | 0.21968 | 0.19399 | 0.19399 | 0.19399 | 8.5716 | 0.19399 | 8.5716 | 0.19399 | 8.5716 |  |  | 1.5361
Sydney North 132 kV | 1.085 | 1.0854 | 1.0854 | 0.85754 | 3.0856 | 0.85754 | 0.85754 | 0.767 | 0.98806 | 0.60028 | 1.1148 | 0.85754 | 0.85754 | 0.79203 | 0.99037 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 | 0.85754 |  |  | 1.5623
Sydney South 132 kV | 1.1822 | 1.1828 | 1.1828 | 0.85021 | 2.8781 | 0.85021 | 0.85021 | 0.77567 | 0.97366 | 0.59515 | 1.1053 | 0.85021 | 0.85021 | 0.79538 | 0.98624 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 | 0.85021 |  |  | 1.5753
Inner Sydney group total MWh | 22.2435 | 22.2462 | 22.2462 | 2.3901 | 32.1455 | 2.3901 | 2.3901 | 2.7506 | 2.7777 | 10.5372 | 3.1071 | 2.3901 | 7.7559 | 7.0203 | 2.7336 | 7.7559 | 2.3901 | 2.3901 | 22.7514 | 2.3901 | 22.7514 | 2.3901 | 39.3516 |  |  | 12.2221
Broken Hill 22 kV | 1.5527 | 1.5527 | 1.5527 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 2.804 | 5.1514 | 8.2922 | 5.171 | 3.9777 | 11.846 | 10.6412 | 4.3817 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 3.9777 | 11.846 | 3.9777 | 11.846 |  |  | 0.2306
Broken Hill 220 kV | 49.266 | 0.93246 | 0.93246 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 0.83397 | 1.5488 | 0.83397 | 1.5488 | 1.1914 | 1.1914 | 1.0723 | 1.3105 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914 |  |  | 0
Broken Hill group total MWh | 50.8187 | 2.4851 | 2.4851 | 5.1691 | 5.1691 | 13.0374 | 5.1691 | 3.6379 | 6.7002 | 9.1262 | 6.7198 | 5.1691 | 13.0374 | 11.7134 | 5.6922 | 5.1691 | 5.1691 | 5.1691 | 5.1691 | 5.1691 | 13.0374 | 5.1691 | 13.0374 |  |  | 0.2306
x
MD (MW) | [9 empty] | 0.7 | 1.3 | [12 empty] | x | bsp# | LF
Canberra 132 kV Note 3 | 478 | 478 | 478 | 435 | 435 | 435 | 435 | 435 | 435 | 304.5 | 565.5 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | x | 13 | 0.55
Williamsdale 132 kV Note 3 | 186 | 186 | 186 | 180 | 180 | 180 | 180 | 180 | 180 | 126 | 234 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | x | 97 | 0.55
Macarthur 132 kV | 298 | 298 | 298 | 162 | 162 | 162 | 162 | 162 | 162 | 113.4 | 210.6 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | x | 44 | 0.47
Macarthur 66 kV | 178 | 178 | 178 | 162 | 162 | 162 | 162 | 162 | 162 | 113.4 | 210.6 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | x | 45 | 0.47
Orange North 132 kV | 153 | 153 | 153 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 100.52 | 186.68 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | x | 63 | 0.74
Orange 66 kV | 62 | 62 | 62 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 34.02 | 63.18 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | x | 64 | 0.54
Taree 33 kV | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16.8 | 31.2 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | x | 80 | 0.47
Taree 66 kV | 49 | 49 | 49 | 47 | 47 | 47 | 47 | 47 | 47 | 32.9 | 61.1 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | x | 81 | 0.53
Beaconsfield 132 kV | 311 | 311 | 311 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 253.12 | 470.08 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 | 361.6 |  | 5 | 0.55
Haymarket 132 kV | 382 | 382 | 382 | 446 | 446 | 446 | 446 | 446 | 446 | 312.2 | 579.8 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 | 446 |  | 33 | 0.48
Rookwood Road 132 kV | 256 | 256 | 256 | 280 | 280 | 280 | 280 | 280 | 280 | 196 | 364 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 72 | 0.48
Sydney North 132 kV | 917 | 917 | 917 | 835 | 835 | 835 | 835 | 835 | 835 | 584.5 | 1085.5 | 835 | 835 | 835 | 835 | 835 | 835 | 835 | 835 | 835 | 835 | 835 | 835 |  | 76 | 0.52
Sydney South 132 kV | 930 | 930 | 930 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 722.82 | 1342.38 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 | 1032.6 |  | 77 | 0.53
Broken Hill 22 kV | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 26.6 | 49.4 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 11 | 0.48
Broken Hill 220 kV | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 15.4 | 28.6 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 12 | 0.75
x
N-1 EUE (mins) | DR | out23_0 | _input0 | basecase | aemovcr | VCR70 | VCR130 | length70 | length130 | MD70 | MD130 | discrateL | discrateH | failrate90 | failrate110 | lives70 | lives130 | ugcostmult5 | ugcostmult25 | lcostcoef70 | lcostcoef130 | lcostexp70 | lcostexp130 | x
Canberra group mins | 2.5511 | 2.5512 | 2.5512 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | 2.5039 | 3.1789 | 3.2046 | 2.6359 | 2.8349 | 2.8349 | 2.6307 | 3.0407 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | 2.8349 | x
Macarthur group mins | 1.2225 | 1.2225 | 1.2225 | 2.5175 | 2.5175 | 4.0277 | 1.3781 | 1.227 | 4.2057 | 2.8804 | 1.1827 | 2.5175 | 2.5175 | 2.3417 | 2.6953 | 4.0277 | 2.5175 | 2.5175 | 2.5175 | 1.3781 | 4.0277 | 1.3781 | 8.8042 | x
Orange group mins | 5.3262 | 3.4921 | 3.4921 | 6.0388 | 6.0388 | 6.0388 | 5.9329 | 4.9087 | 7.0229 | 6.9194 | 5.4587 | 5.9329 | 6.0388 | 5.6152 | 6.3399 | 6.0388 | 6.0388 | 6.0388 | 6.0388 | 6.0388 | 6.0388 | 6.0388 | 6.0388 | x
Taree group mins | 13.6857 | 13.691 | 13.691 | 14.6729 | 14.6729 | 31.8455 | 10.9289 | 11.7665 | 17.2015 | 16.1056 | 13.9015 | 14.6729 | 14.6729 | 13.5018 | 15.8527 | 14.6729 | 14.6729 | 14.6729 | 14.6729 | 10.9289 | 14.6729 | 10.9289 | 31.8455 | x
Inner Sydney group mins | 1.4291 | 1.4292 | 1.4292 | 0.57346 | 1.7412 | 0.57346 | 0.57346 | 0.58761 | 0.58867 | 1.276 | 0.46277 | 0.57346 | 0.78404 | 0.75518 | 0.58694 | 0.78404 | 0.57346 | 0.57346 | 1.3726 | 0.57346 | 1.3726 | 0.57346 | 2.024
Broken Hill group mins | 86.3048 | 4.5913 | 4.5913 | 9.3259 | 9.3259 | 22.9153 | 9.3259 | 6.6814 | 11.9703 | 23.086 | 9.234 | 9.3259 | 22.9153 | 20.6288 | 10.2293 | 9.3259 | 9.3259 | 9.3259 | 9.3259 | 9.3259 | 22.9153 | 9.3259 | 22.9153

## EUE_distribution
basecase
202.6739
190.7062
115.7279
115.7279
114.0826
78.6751
64.7067 | >60
51.3629
50.5058
48.8967
45.3928
42.0547
41.8477
41.5795
40.4451
40.3084
39.6402
39.5921
32.5437
32.355
31.4392
31.1838
30.8889
27.8429
27.0129
25.6416
24.9456
23.8624
23.4378
22.5551
21.4651
20.4185 | >20
19.5683
18.8348
18.6784
18.6678
18.6044
18.3068
18.1787
17.6257
17.1457
16.973
16.5316
13.8431
13.8319
13.4757
13.335
13.3071
13.1682
12.6923
12.3191
12.3126
12.3026
12.1259
11.8254
11.6612
11.056
10.8037 | >10
9.5976
9.3239
8.2952
6.9778
6.6999
6.446
6.272
5.4189
5.1201
5.1104
4.9422
4.8858
4.8726
4.6376
4.5754
4.3323
4.1848
4.0406
4.005
3.9457
3.9104
3.7783
3.7225
3.6504
3.367
3.3616
3.2619
2.8866
2.6067
2.0051
1.963
1.6213
1.3362
1.3125
1.1895
1.0718
0.98326
0.80316
0.77235
0.74632
0.33438
0.26592